## Slide 1: Hardware Platforms for ESS ICS
Timo Korhonen
Chief Engineer, Integrated Control Systems Division
European Spallation Source ERIC
www.europeanspallationsource.se

## Slide 2: Outline
Performance ranges and solutions
High-speed platform
  General strategy
  Common Platform development & status
Middle-level: EtherCAT
Industrial I/O
“the rest”

## Slide 3: Hardware strategy
Three levels of performance
MTCA
  High-speed front-end processing
  Digital Frontend Platform
EtherCAT
  mid-range, beam synchronised I/O
  Used mainly as a fieldbus
PLC
  Industrial, process I/O
  Safety systems, high reliability
Selection of platform based on requirements and cost
Signal speed
10 Hz
1 Hz
0.1 Hz
100 Hz
1 kHz
10 kHz
100 kHz
1 MHz
10 MHz
Electronic front-end platform
EtherCAT
Industrial automation (PLC)

## Slide 4: High Performance Applications
Performance requirements (very shortly)
  Support 14 Hz operation
    Good integration with timing
  Acquisition (ADC sampling) at ~100 MSPS
    2.86 ms pulses@14 Hz : 4% duty cycle
    a lot of raw data; process locally but prepare for exposing the data for troubleshooting purposes
  Interfaces to machine protection/interlock are crucial
MTCA.4 was selected as the standard for this range
  Still new and unproven in operation
  Work needs to be done to ensure:
    Maintainability, interoperability
    Development and long-term sustainability

## Slide 5: High-speed Digital Controller Board
A general-purpose board in two variants
  Pure FMC carrier with digital/serdes RTM
  Analog I/O (10 ch) through Zone 3, single FMC slot
    To accommodate existing designs
    On-board ADCs with a FMC interface
All fast systems have agreed to use this platform
  As far as we can keep the agreed delivery timeline
    Fallback solutions have been identified
  Beam Instrumentation systems
    BPM, BLM, BCM, WS, etc.
  RF systems
    LLRF, RF Fast Interlock
    Early deployments may be using other hardware

## Slide 6: Digital Controller Board for ESS
In-kind contribution from Switzerland (PSI)
  With an industry partner (IOxOS SA)
Port of an existing architecture to MTCA.4 hardware
  Use new generation components
  Reuse existing designs (PSI & others)
  Linux OS, EPICS software
    CPU on-board (Freescale QorIQ T2081)
  Xilinx FPGA (Kintex Ultrascale)
    Firmware library/framework TOSCA-III
      Network-On-Chip, non-blocking PCI Express
    Source code available to all ESS partners and licensees (very liberal but not fully open source)
  Schematics, board layouts, etc. included

## Slide 7: Digital Controller Board
FMC carrier board
  Readily integrated FMCs available
    ADC 250 MSPS 16-bit, 1 GSPS 4 CH 12-bit, etc.
    Integration of new functions (fairly) easy
  Modular firmware library: use same application with different FMCs, common base memory map
CPU on-board – why?
  Processing “blade”. Use standalone when required, use as AMC when integration required.
  Better scaling than with a single central CPU
    Multiply simple units rather than integrate functions
  External (more powerful) CPU can be easily added to a system

## Slide 8: Board block diagram - simple
Four main functional blocks
  CPU, Central FPGA
  Power-On FPGA enables flexible FPGA management and powering on of the board
  MMC handles the MTCA infrastructure

## Slide 9: Block diagram – more details

## Slide 10: X-ray view of the board (FMC variant)
No pictures of the final hardware yet. We expect the first boards in 1.5 to 2 months.

## Slide 11: Middle-range I/O
High-end platform is expensive and centralized
  Use only where needed
Some applications still need time synchronization
  Especially in a pulsed machine!
  PLCs are not ideal for this (asynchronous cycle times)
EtherCAT is a good solution for this range
  Uses Ethernet cabling, special protocol
  Can run on a PC or MTCA IOC
  Loop times of several kHz possible
  Distributed I/O (reduce cabling)
  Cost effective
  Many I/O modules, several manufacturers
(Slowly) gaining popularity in the EPICS community

## Slide 12: EtherCAT features
EtherCAT is a master-slave fieldbus architecture
  Uses Ethernet cabling, distributed I/O modules
  A single frame passes through the EtherCAT loop
  All slave modules have to process the frame on the fly (no store&forward)
    Slave modules typically use FPGAs to process the frames
    Low and predictable latency
EPICS drivers exist in two variants
  One from Diamond, one from PSI
    Take a look at the presentation of Dragutin Maier-Majnolovic in the Lund/ESS EPICS meeting

## Slide 13: ESS use cases for EtherCAT
Distributed I/O
  Systems on HV deck (minimize components on deck, isolate electrically)
  Reduce cabling when I/O points are located far apart
Motion control
  TwinCAT PLC for coordinated motion
  MTCA or industrial PC for single-axis, simple motion
    Simplifies system architecture
Cross-system integration
  Feed global time from main timing system into EtherCAT loops (e.g., motion control) – clean synchronization
  Pull EtherCAT data to e.g. MTCA systems
  EtherCAT Slave FMC in development as an in-kind project

## Slide 14: Industrial I/O
No surprises here: use PLCs for most industrial-type I/O
  High reliability
  Widely known and deployed in partner labs and industries
  A huge selection of I/O modules available
Selected a manufacturer via an open call for tender
  Siemens S7-1500 series is the ESS standard
  For regular and safety applications
One vendor/manufacturer policy
  Reduce development and maintenance costs
    One skillset, reduced stock of spares

## Slide 15: “Other” I/O
There is still a large number of devices not covered yet
  Serial devices
    Use MOXA – almost de-facto standard
  Ethernet-based devices
    Ethernet as a fieldbus, use StreamDevice & ASYN
  Cameras
    GigE, 10GBE, CameraLink(HS)
    EPICS AreaDetector supports a large device base
  Motion control
    EtherCAT-based, in two variants, roughly divided:
    Beckhoff TwinCAT for demanding motion control
    Open source master for single-axis, straightforward applications (“drive to position x and stop”)

## Slide 16
Questions?