## Slide 1: Building EPICS Databases From Excel
Jim Stevens
APS Controls Group
EPICS Collaboration Meeting; Oak Ridge National Laboratory
September 2016

## Slide 2: Why Build Databases From Excel?
Huge # of Process Variables
Discrete Records (ai, bi, longin)
Unique Process Variable Names
Simplify Process Variable Selection
Simplify Database Changes
Simplify Troubleshooting

## Slide 3: APS Experimental Beamline Station

## Slide 4: Background
APS Experimental Beamline Personal Safety System (PSS):
35 “Sectors” of Experimental Beamlines

## Slide 5: Background
APS Experimental Beamline Personal Safety System (PSS):
35 “Sectors” of Experimental Beamlines
ID = Insertion Devices BM = Bending Magnets

## Slide 6: Background
APS Experimental Beamline Personal Safety System (PSS):
35 “Sectors” of Experimental Beamlines
ID = Insertion Devices BM = Bending Magnets
Maximum of Six Stations Per Beamline

## Slide 7: Background
APS Experimental Beamline Personal Safety System (PSS):
35 “Sectors” of Experimental Beamlines
ID = Insertion Devices BM = Bending Magnets
Maximum of Six Stations Per Beamline
Two PLC’s Per Beamline to Monitor Safe Entry & Exit
  * Chain ‘A’ Allen-Bradley PLC5’s
  * Chain ‘B’ General Electric Fanuc PLC’s

## Slide 8: Background
APS Experimental Beamline Personal Safety System (PSS):
35 “Sectors” of Experimental Beamlines
ID = Insertion Devices BM = Bending Magnets
Maximum of Six Stations Per Beamline
Two PLC’s Per Beamline to Monitor Safe Entry & Exit
  * Chain ‘A’ Allen-Bradley PLC5’s
  * Chain ‘B’ General Electric Fanuc PLC’s
Doors, Crash Buttons, Limit Switches, Strobes, Water Flow, etc.

## Slide 9: Background
APS Experimental Beamline Personal Safety System (PSS):
35 “Sectors” of Experimental Beamlines
ID = Insertion Devices BM = Bending Magnets
Maximum of Six Stations Per Beamline
Two PLC’s Per Beamline to Monitor Safe Entry & Exit
  * Chain ‘A’ Allen-Bradley PLC5’s
  * Chain ‘B’ General Electric Fanuc PLC’s
Doors, Crash Buttons, Limit Switches, Strobes, Water Flow, etc.
70 X (# of Stations) X (# of Doors) X (# of Buttons) X (# of Switches) etc.
The # of EPICS Database Combinations is Staggering!!

## Slide 11: 03-ID PSS Control Display

## Slide 12: EPICS From Excel Database “Ingredients”
Excel Formatted Spreadsheet
Record Template Files (ai,bi,longin…)
Database Makefile
Perl Script “PSSxls2db.pl”
‘Spreadsheet-ParseExcel’ module

## Slide 13: PSS Excel “Worksheet” Format
Name Address Description

## Slide 14: Binary Input Record Template File
~ioc/pss/2/pssApp/xls/PA_BinaryInput.template
record(bi, "PA:$(xx)$(yy):$(name)") {
field(DESC, "$(desc)")
field(SCAN, "I/O Intr")
field(DTYP, "Ab Dcm")
field(INP, "@PA:$(xx)$(yy):dcm.$(dcmAddr)")
field(ZSV, "MAJOR")
field(ZNAM, "OFF")
field(ONAM, "ON")
}
Name Address Description

## Slide 15: Database Makefile
~ioc/pss/2/pssApp/Db/Makefile
DB += 03ID.db
PA_01BM_IO_TEMPLATE = PA_BinaryInput.template
include $(TOP)/configure/RULES
#----------------------------------------
# ADD RULES AFTER THIS LINE
PA_TEMPLATES+=PA_IO=$(PA_$*_IO_TEMPLATE)
$(COMMON_DIR)/PA_%.db:$(TOP)/xls/%.xls
@$(RM) $@ $(notdir $@)$(DEP)
@$(PERL)$(TOP)/xls/PSSxls2db.pl $@ $< $(PA_TEMPLATES)

## Slide 16: Perl Script
~ioc/pss/2/pssApp/xls /PSSxls2db.pl
use strict;
use Spreadsheet::ParseExcel;
use File::Basename;
# Convert excel worksheet name to template file ID.
my %sheetID=()
$sheetID{‘Analog’} =‘ANALOG’;
$sheetID{‘IO’} =‘IO’;
$sheetID{‘Beamline|PLC Status’} =‘PLC’;
$sheetID{‘Warning Bits|PLC Bits’} =‘WARNING_PLC_BITS’;
$sheetID{‘Fault|Trip Bits’} =‘FTBITS’;
$sheetID{‘FIFOs’} =‘FTW’;

## Slide 17: Perl Script
~ioc/pss/2/pssApp/xls/PSSxls2db.pl
# Loop over each line of template file
my $newline;
foreach $line (@lines) {
$newline = $line;
$newline = ~s/\$\(name\)/$name/;
$newline = ~s/\$\(desc\)/$desc/;
$newline = ~s/\$\(dcmAddr\)/$dcmAddr/;
$newline = ~s/\$\(prec\)/$prec/ if $prec;
$newline = ~s/\$\(aslo\)/$aslo/ if $aslo;
$newline = ~s/\$\(fanAddr\)/$fanAddr/;
print OUT $newline
Name Address Description

## Slide 18: Perl Script
~ioc/pss/2/pssApp/xls /PSSxls2db.pl
# Loop over each line of template file
my $newline;
foreach $line (@lines) {
$newline = ~s/\$\(prec\)/$prec/ if $prec;
$newline = ~s/\$\(aslo\)/$aslo/ if $aslo;
print OUT $newline

## Slide 19: Perl Script
~ioc/pss/2/pssApp/xls /PSSxls2db.pl
# Loop over each line of template file
my $newline;
foreach $line (@lines) {
$newline = $line;
$newline = ~s/\$\(name\)/$name/;
$newline = ~s/\$\(desc\)/$desc/;
$newline = ~s/\$\(dcmAddr\)/$dcmAddr/;
$newline = ~s/\$\(prec\)/$prec/ if $prec;
$newline = ~s/\$\(aslo\)/$aslo/ if $aslo;
$newline = ~s/\$\(fanAddr\)/$fanAddr/;
print OUT $newline

## Slide 20: Database Binary Input Record
~ioc/pss/2/pssApp/db/03ID.db
record(bi, "PA:$(xx)$(yy):FES_PS1_CLOSED_LS") {
field(DESC, "Front End PS1 Closed Switch")
field(SCAN, "I/O Intr")
field(DTYP, "Ab Dcm")
field(INP, "@PA:$(xx)$(yy):dcm.T6[32,1]")
field(ZSV, "MAJOR")
field(ZNAM, "OFF")
field(ONAM, "ON")
}

## Slide 21: Why Build Databases From Excel?
Huge # of Process Variables
Discrete Records (ai, bi, longin)
Unique Process Variable Names
Simplify Process Variable Selection
Simplify Database Changes
Simplify Troubleshooting

## Slide 22: Why Build Databases From Excel?
Simplify Database Changes
Simplify Troubleshooting

## Slide 23: Reference Documents
Spreadsheet-ParseExcel
  https://github.com/runrig/spreadsheet-parseexcel
EPICS Application Developer’s Guide
  EPICS Base Release R3.14.12.5
XLS EPICS DEMO DATABASE
  xls.tar.gz

## Slide 24: Credits
Ned Arnold
Janet Anderson
Andrew Johnson
Mike Fagan
Van Nguyen
Phil McNamara