## Slide 1: Solving Process Instrumentation Challenges for the ESS Target Safety System
Ola Ingemansson
Electrical & Instrumentation Engineer
European Spallation Source ERIC
2019-10-15

## Slide 2: Outline
Introduction
  ESS overview
  Target Safety System
Process Instrumentation Selection for TSS
  Sourcing equipment
  Compatibility
  Resistance to environment
  Obsolescence
  Solving challenges
  Documentation requirements
Summary

## Slide 3: The ESS facility layout Main parts
Target
Proton Linear Accelerator
Pulse frequency 14 Hz
Proton energy 2 GeV
Beam power, time averaged 5 MW, within pulse 125 MW
Beam current 62,5 mA
Neutron Science Systems
22 planned and budgeted neutron scattering instruments
Neutron beam line lengths ranging from 10 m to 150 m from source
The European Spallation Source (ESS) is a multi-disciplinary research center based on the world’s most powerful neutron source

## Slide 4: ESS Target Station
5 MW long pulse spallation source
  2.86 ms proton bunch at 14 Hz rep rate
  Raster pattern where protons incident upon Target wheel
Rotating tungsten target
  5.4 tons (4900 kg) wheel only, (11 tons wheel + shaft)
  rotating at 23.3 rpm (sector receives beam pulse every 2.4 seconds)
  5 year lifetime, He gas cooled
Cold Moderators
    Liquid hydrogen with 2-5 year lifetime
Inventories
  High power beam impacting the tungsten target will create an inventory of nuclides
  Primary inventory is in wheel (monolith and storage in active cells)

## Slide 5: Key features of the ESS Target Station
Helium cooling of target material
Mass flow 3 kg/s
Pressure 11 bar
Temperature inlet/outlet 40 °C/240 °C
proton beam
proton beam window
proton beam instrumentation plug
Moderator and reflector
target wheel
neutron beam extraction port
monolith vessel
target monitoring plug
Rotating solid tungsten target
36 sectors
Mass, total 11 tonnes, with 3 tonnes of W
Rotates 23.3 rpm, synchronized with pulsed proton beam 14 Hz
Moderators
Provisional locations of moderators above and beneath the target wheel, i.e. monolith centre
1st MR plug exploits the upper space, offering:
  Cold, 30 mm high, liquid H2 moderators, 17 K
  Thermal, 30 mm high, H2O moderator, 300 K
Diagnostics and instrumentation
Controlled and integrated commissioning and operation of the accelerator and target
Fluorescent coating of PBW and target front face
Optical paths, grid profile monitor, aperture monitor
Wheel monitoring including position, temperature, vibration, as well as internal structure
Target Safety System
Monitors target coolant flow, pressure and temperature, monolith pressure, & target wheel rotation
Prohibit beam on target if parameters are outside specified limits

## Slide 6: Target Safety System, TSS Role
Deep defense (C.5 & C.6)
What is the role of the TSS?
The TSS is an independent monitoring interlock system, it is a safety SSC in the Safety Group that acts on DiD Level 3 to:
  Protect the public from exposure to unsafe levels of radiation and prevent the release of radioactive material beyond permissible limits
  Bring the target into a safe state in case of an abnormal event from the radiation safety point of view
    The safe state, from the TSS point of view, is defined as no beam on the target
The TSS handles only radiation safety, not ODH, electrical hazards, fire, etc.

## Slide 7: TSS Context: ESS Radiation Safety
Where does TSS fit within overall Target Radiation Safety Strategy?
  TSS is part of our set of tools
Outcome of Radiation Safety Hazard Analysis for Target Station systems includes:
  Identification of safety functions
  Identification of safety SSCs (structures, systems, and components) and safety-related SSCs
System
design
PSS
TSS
Administrative
Controls
Operational
Group
Controls
BPCS
MPS
Zoning
Safety
Culture
Site
Monitoring
Security
Contributors to Radiation Safety

## Slide 8: Target Safety System (TSS) general overview
3 channel, 2 train safety system
  2 sub relay based trains, performs 2oo3 voting
  1 PLC based train, performs 2oo3 voting
Affects 2x2 actuators
  By breaking up the power supply to the RFQ and Ion-Source
Accident analysis points out 5 conditions to supervise
  Helium mass Flow, He ṁ
  Helium Temperature, He T
  Helium Pressure, He P
  Monolith Pressure (Vacuum), Mo P
  Wheel Rotation Supervision, Wh ω

## Slide 9: General Overview
This presentation focuses on the input side, conditions
TSS Instrumentation
Monitors
Helium pressure (He P)
Helium temperature (He T)
Helium mass flow (He F)
Wheel rotation (Wh w)
Monolith pressure (He P)

## Slide 10: TSS General Overview
Location

## Slide 11: TSS General Overview
Location

## Slide 12: TSS General Overview
Location
Monolith cell about 10 meters in diameter
Triangular room about 15 meters / side
Utility room about 15 meters deep & 20 meters wide
We move in to the TSS

## Slide 13: Challenges for instrumentation selection
Must be able to meet regulatory requirements
Must be able to meet environmental conditions
  involves qualification of instruments
Must be able to monitor necessary parameters on the processes

## Slide 14: 1: Sourcing equipment
Set up a technical specification for each field object to be used in the safety solution
  Avoid brand-specific specifications in the document
Ask plants that are operating within a similar regulatory context for their choice of suitable equipment
  What do “you” use?
  What is your experience of brand X &Y
    Fault tracing
    User-friendly
    Availability
    Supplier’s ability
  How did you perform the environmental qualification?
Try to find a number of suppliers for each condition in order to create a competition situation
Apply the KISS-rule, Keep It Simple Stupid

## Slide 15: 2: Compatibility
SSM design rules
  Structures, systems and components of importance to radiation safety shall be based on proven technologies and proven methods, and be tested before application.
  The time during which the facility’s structures, systems and components of importance to radiation safety can be used in a safe manner shall be determined in the design
  Facility structures, systems and components of importance to radiation safety shall be designed so that sufficiently high quality can be maintained throughout the intended lifetime
SSM design rules with respect to Common Cause Failure (CCF)
  a. Functions are performed in physically different ways.
  b. Functions are performed by different Technologies/design solutions.
  c. Structures, systems or Components are from different manufakturers.
  d. Structures, systems or Components are installed on different occasions.
  e. Structures, systems or Components are verified, validated, maintained and tested at different times and by different personnel.
  Conclusion
    This will not allow us to use the same brand for diverse functions, i.e. Monolith Pressure & Helium Pressure
Will chosen component fit into the design rules?

## Slide 16: 2: Compatibility
We have to be observant with respect to which internal components are in use
  Honeywell micro switches are very commonly used
  AD-converters are very commonly used
  Try, if possible, to pick different types of measurement i.e. Pressure switches: Bourdon type vs Diaphragm type
We have to make sure that chosen equipment can work together with other ESS equipment
  What power source do we need for transmitter power supply, 24VDC?
  Will the microswitches be able to handle the electrical currents possible in the solution?
  Proven technology
Aim to use Commercial-off-the-shelf components, COTS
  Proven design, Components with a good record, Robust components
  Base our choice on experience
    Brand, supplier, establish a contact with the supplier, meet them, visit them, invite them
Will chosen component fit into the design rules?

## Slide 17: 3: Resistance to environment
Dose mapping (normal operation) results in a zoning
Area of interest is level 110
Conclusion
  No active electronics in red areas
Will the chosen equipment withstand the environment?

## Slide 18: 3: Resistance to environment
Environmental qualification – Performed in two steps
Pre-qualification performed on test objects
  Select institute (RISE in Sweden) to perform the tests
    Perform Moisture pre-test
    Perform Heat/cold pre-tests, cycling the temperature
    Perform vibration pre-test
    And any other tests necessary according to the technical specification
  Evaluate the results
    Make a pre-selection as input into procurement process
    This may result in going back a step and finding other solutions/suppliers
Will the chosen equipment withstand the environment?

## Slide 19: 3: Resistance to environment
Environmental qualification – Left to do!
Purchase the components intended to use
  Include an estimation of the number of spares for 10-15 years of use, and include one test object
  Qualify the batch purchased by
    Repeat environment tests on one unit of each type on one randomly selected test object
    Evaluate results
    Document all tests and results
  Output of the process is a qualified batch of process instruments according to the chosen standard – IEC 61226 (nuclear standard)
This is our present state!

## Slide 20: 4: Obsolescence
One tricky part is to handle Obsolescence
  How do we ensure a stable supply of replacement parts? We can’t!
  We intend to use this strategy!
    Choose a well known brand
    Choose a well known supplier, establish a good relationship
    Ensure that we have spares for a long time, estimate the need for 10-15 years
    If a component breaks down “too” often, find a new one and perform the environmental qualification again
Will we be able to supply ESS with components at least the first 10 years?

## Slide 21: Solving challenges
Helium Mass Flow Measurement, Challenges
  Radiation environment
    Solved by moving transmitters away from direct process related areas
  Mass flow
    Solved by one unit measuring both static and dynamic pressure, add a temperature measurement, calculate mass flow locally
  Pressure drop
    Solved by using venturi tube type of measurement
Solutions

## Slide 22: Solving challenges
Helium Temperature Measurement, Challenges
  Radiation environment
    Solved by using Pt-100 sensors, a Platinum wire
  Response time issues
    Solved by not having a thermo well and by taking down outer diameter of sensor as far as possible, 2.5 to 3mm thick sensors, to give response time of about 10 seconds
Solutions

## Slide 23: Solving challenges
Pressure & Vacuum Measurements in Helium & Monolith areas, Challenges
  Radiation environment
    Solved by moving pressure switches away from direct process-related areas
  CCF issues
    Solved by choosing different brands and suppliers of the two conditions
Solutions
Enclosure
Switching element on stainless steel bracket
Terminal block standard
Electrical conduit connection:
-Pg 13,5 -M20 x 1,5 -3/4 NPT (F) -1/2 NPT (F)
Cable gland (Option “C”)
Earth terminal (Standard)
Spring
Pressure sensor body
Process connection (Wetted)

## Slide 24: Solving challenges
Wheel Rotation Measurement, Challenges
  Hard neutron and gamma radiation environment
    Solved by using radiation resistance cabling
    Solved by planned maintenance to change out equipment every 24 months
      Or more often if needed
  Trouble finding more than one supplier
    Not solved
Solutions

## Slide 25: 5: Documentation Requirements
Buy the test documentation packages from the supplier
Be sure to require information on how often the component should be replaced
  Ideally not during the lifetime of ESS!
Require traceability from the manufacturing process
  One reason for us to use a supplier from the nuclear industry is that they are used to this and have ready-made documentation packages tailored to nuclear requirements
Document FAT, SAT, make the supplier a part of this
Document every decision taken
Key document to keep in perfect order is the technical specification
Make sure that components are inserted into the Enterprise Asset Management system (EAM)
  Will help us to keep the traceability throughout the life cycle of the components
Often forgotten in purchasing safety equipment!

## Slide 26: Summary
We buy “Commercial-off-the-Shelf” components & rely on proven design
  This will secure a stable supply of spares if needed – at least the first years of running the ESS
We aim to have at least two alternatives on every measurement type
  We go on a public procurement when buying the equipment
    In order to create a competition situation
We perform the environmental qualification ourselves, using an independent test institute
  We shall attend when tests are performed
And we have to be sure to document every step taken and the decisions that were made
  The test institute will provide us with a test report
    We will rely on the test institute quality system with respect to test setup, interpretation of the test standards and how to perform the tests
    We will take part in reviewing the test report
Chosen strategy

## Slide 27: Example of qualification test
A small movie to give you an idea of environmental qualification!
  Vertical shaking
    The whole sequence is 3-200Hz and then 200-3Hz
    This is repeated 10 times
    Shown here is 20-45Hz
    Then shaking in X-direction is done
    Then shaking in Y-direction is done
Thank you for your attention!