## Slide 1: Controls and Protection Systems
Karen S. White
Controls Group Leader
2/16/16

## Slide 2: Outline
Scope
Availability
Infrastructure
Process Controls
Controls Hardware
Controls Software
Protection Systems

## Slide 3: Integrated Control System Overview
ICS Scope: Controls, Timing and Protection Systems
      Accelerator Instruments (PPS, Vacuum, Tools)
      Target Conventional Facilities
      Cryogenics Test Facilities
Large, distributed system based on the Experimental Physics and Industrial Control Systems (EPICS) toolkit and Control System Studio (CSS)
EPICS provides a flexible, layered architecture and integrates a variety of front end platforms
Scalable, distributed architecture is extensible (PPU/STS)
  new devices, capability, functionality can be added as needed
Emphasis on commercial, configurable, collaborative solutions

## Slide 4: System Performance - Availability
Chart: 
| FY07 | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14 | FY15 | FY16-Q1
ICS Availability | 0.9683 | 0.98782 | 0.9793 | 0.99358 | 0.99339 | 0.99576 | 0.98613 | 0.99688 | 0.9962 | 0.99263
90% Availability goal | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
95% Availability Goal | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
PLC/firmware issues
PPS grounding error

## Slide 5: Controls Infrastructure – Cyber Security
ORNL Office of Independent Oversight conducted an assessment of cyber security of industrial control systems (ICS) at HFIR and SNS to safely determine the vulnerabilities, risk and mitigations in place
Assessment team was directed to focus on:
  The security posture of ICS implementations with respect to threats from the ORNL enterprise network and the ORNL supplied visitor network
  The security posture of ICS implementations with respect to threats originating from remote access

## Slide 6: Controls Infrastructure – Cyber Security
Preparing for Assessment
  Conducted self assessment using DHS ICS-CERT Cyber Security Evaluation Tool (CSET) based on NIST 800-82
  Used the results of this analysis to make cyber improvements to our infrastructure
    Completed conversion to more rigorous account management
    Added Intrusion Detection System (IDS)
    Audited all accounts and role authorizations including access to server rooms
    Replaced aging, less capable firewalls
    used to isolate the controls network

## Slide 7: Controls Infrastructure
Audit concluded
  “SNS is doing a good job of securing their systems and equipment”
  “Decision to align controls with NIST Special Publication 800-82 (Guide to Industrial Control System Security) puts SNS on the right track to providing consistent, verifiable security”
OFIs
  Until moving to a tool for maintaining the PLC logic files, extra care should be taken to verify any changes in the PLC logic before it is put into use
  Move the logbook status entries behind the password system or restrict cyber sensitive information from being placed on the publicly readable logbook
  The EPICS system should have a security assessment
Notes: Use digital signatures to verify that an e-mail is legitimate for functions like authorizing Prox card access

## Slide 8: Process Controls Progress on Obsolescence
Instrumentation for High Radiation Areas
  Worked with vendors to design and produce pressure and flow instruments for
    High radiation area water loops
    Ultra high radiation area mercury loops
  First units installed in February 2016
Water Loop Flow
Mercury Loop Flow

## Slide 9: Process Controls Progress on Obsolescence
Remote Handling System
  Identified a potential vendor for complete mechanical and controls replacement and obtained a budgetary cost estimate
  Established working group to identify requirements
  Camera controller upgraded to a modern matrix controller
Existing
Proposed

## Slide 10: Process Controls Progress on Obsolescence
Chiller Controls
  Working on replacement of Trane BACnet communication module
Vacuum (AIP-35)
  Vacuum upgrade also replaces obsolete controls components: gauge controllers, ion pump controllers, PLCs
  New controls installed for DTL1-6 July 2015
  CCL 1-4 cables installed Jan 2016
  CCL1-4 vacuum and controls installation scheduled for June 2016

## Slide 11: Process Controls Sustaining Control System Performance
Cryogenic controls
  Installed automatic transfer switches for power to controls equipment
  Systematically replacing cryomodule heater power supplies, 8 units each outage
  Added PLC interlock to stop turbines 3 and 4 if a first stage compressor trips (4K Cold Box)
  Replaced warm compressor gas management PLC and I/O modules
  Upgraded PLC firmware
  Added warm compressor skid trip data capture feature

## Slide 12: Process Controls Supporting Accelerator Development
Implemented motion controls for new primary stripper foil mechanism
ITS - Controls for LEBT, RFQ, MEBT water and vacuum

## Slide 13: Process Controls Supporting CF Development
CUB CF Improvements
  Integrated cooling tower water make-up system and weather station
Target CF Improvements
  Sensible Chilled Water System controls upgraded to provide multiple pump modes

## Slide 14: Process Controls Improving Development Process
Configuration Management of PLC Code
  Previously, engineers informally managed PLC code versions on a shared SAMBA server
  This method allow inconsistencies that could make it difficult to identify the correct version of code to load; lacked structure and documentation
  Purchased commercial tool, “Factory Talk AssetCentre” to manage versioning of PLC code
  Migration of PLC files to AssetCentre is nearly complete, only CHL files left to move
  Protection Systems team will evaluate tool for their use
  Tool availabile to other SNS groups

## Slide 15: Controls Hardware Progress on Obsolescence
Timing System – continued deployment of new modules, recovering spares
  Timing receiver - replaces old utility and trigger modules
    Deployed in HPRF FY15 (15 units)
    Deployed in LLRF FY16 (55 units)
    66% timing receivers replaced
  Timing fan-outs
    100% Fiber-to-Fiber fan-outs replaced
    68% Fiber-to-Copper fan-outs replaced
    85% Timing infrastructure replaced
  New Timing Master operating in the ITS

## Slide 16: Controls Hardware Progress on Obsolescence
Machine Protection System
  Difficult to support; many obsolete components
  Limited ability to repair existing platforms
  System is overly complex
  Redesign in progress (AIP-39) to address obsolescence, simplify system and ensure expandability for PPU/STS
Power supply interface and controller cards (PSI/PSC)
  Obsolete components limiting ability to make repairs or purchase replacement cards
  Need to work with EE/PS to develop a plan to address
  New power supplies free up some older modules to be used as spares

## Slide 17: Controls Hardware Supporting Accelerator Development
New LEBT Chopper Controller
  Ramp down functionality added, supports “sustaining 1.4MW” goal
  Integrates DBCM fast MPS interface via rear transition card for better errant beam control; reduces MPS response time 7.6 μS
  Includes control interface and replaces “black box” controller
  Uses new timing receiver card with minimal modification

## Slide 18: Controls Software Supporting Accelerator Development
Provided EPICS integration for many accelerator projects
  Ion Source: spectrometer timing, new power supplies
  E-kicker power supplies
  New serial power supplies
  New features and PanelView upgrade for RF transmitter
  DTL vacuum upgrade (AIP-35)
  CHL He inventory tool
  MKS 937B vacuum gauge controller
  TCP350 turbo pump
  LEBT chopper controller

## Slide 19: Controls Software Supporting Accelerator Development
EPICS integration for AIPs
  New HVCM controller (NI) (AIP-34)
  DTL vacuum upgrade (AIP-35)
  ITS (AIP-30)
    Power supplies, signal generators, RF, oscilloscopes
    RFQ, LEBT, MEBT Vacuum

## Slide 20: Controls Software Sustaining Control System Performance
Target alarms converted to CS-Studio alarm handler (BEAST)
Upgraded IOCs (MVME-5500): HPRF (15), Cryogenic Moderator (1)
Improved EPICS support for new timing master and developed device support for new timing receiver for LLRF IOCs
  Device support for MPS, OMS-58, and Beckoff for new IOC (MVME-5500)
  Improved cryogenic IOC directory structure and version management

## Slide 21: Controls Software Tools
Need to replace aging display manager (EDM)
CS-Studio BOY can render many EDM screens
  EDM converter collaboration w/ Diamond Light Source
  BOY used extensively on SNS beamlines
  Performance will likely not scale for SNS accelerator
  Analysis exposed internal limitations (burdens UI thread, tied to limiting technology)
EDM displays and auto-converted CS-Studio versions
Notes: Graphical editing framework
Standard Widget toolkit

## Slide 22: Controls Software Tools
Display Builder- “Looks like BOY”, but improved, modular design
  Model: Widgets and their properties, file format
  Representation: On-screen objects in JavaFX
  Performance: Handles PVs and scripts in background threads
  Started mid-2015, first release end-2016
  Handles basic instrument displays, better performance
  Currently implements 1/3 of BOY widgets with minimum features
BOY
Display Builder

## Slide 23: Protection Systems Improvements Power Supply Grounding Isolation
Grounding issue discovered July 2013 in PPS CCR rack
Defect was corrected, grounding was evaluated system wide and improvement plan developed
  July 2015 – Isolated CCR, replaced racks
  January 2016 – Isolated klystron gallery cabinet
  June 2016 - Isolate HEBT cabinet
  January 2017 - Isolate Ring cabinet power, replace front end cabinets
  July 2017 - Isolate RTBT cabinet power
  January 2018 - Isolate Target PPS power

## Slide 24: Protection Systems Improvements PPS CCR Rack Upgrade
Replaced 4 CCR Protection System racks with pre-assembled and pre-tested units
Demo and replacement took less than one day
Units ready for integration testing in three days
Although functionally equivalent, new design incorporates safety, maintainability, and human factor improvements
Notes: Racks were replaced to eliminate error found in July 2013
Replacing racks in-toto minimized required SNS down time and maximized test and integration time
Some Improvements:
Replaced obsolete electronics
All 120VAC is confined to one rack. Access to all other racks has safe voltages
Re-arranged panel layout to better reflect SNS operating modes
Improved wiring methods, diagnostics, and modularity significantly improves repair time

## Slide 25: Protection Systems Sustainability
Documentation
  Generated : >250 new and >200 revised as-built drawings since January 2015
Continuing to validate protection systems’ configuration basis
Updating procedures
  New radiation monitor calibration procedure takes ½ time
Analyzing failure modes and statistics
Plan to upgrade obsolete linac oxygen monitors
  Use long-life sensors, eliminates annual sensor replacement (>$40k/year)
  Reduces maintenance from ~40 hours to 4 hours per year

## Slide 26: Protection Systems Sustainability Simplifying Infrastructure
Removed electrical safety interlock function from PPS
Eliminated interlocks for 464 of 468 power supplies, leaving only interlocks 4 used for beam containment
  ORNL/SNS relies on LOTO for hazardous energy control
Eliminates requirement to manage power supplies as CECs
Reduces time needed for PPS certification by ~20%

## Slide 27: Protection Systems Sustainability Simplifying Infrastructure
    Consolidate PPS architectures and equipment
      Lack of standardization on instrument PPS’ increases maintenance effort and spares cost
      Instrument PPS prototype defined as the benchmark for evaluating existing beamlines and prioritizing upgrades
Collaborated with Electrical and IDAC groups to create standard secondary shutter motion control assembly/PPS interface for EPICS beamlines
  Eliminated PPS interlocks for some sample robots and detector motion controls

## Slide 28: Protection Systems Supporting Accelerator Development
Developing PPS for ITS
Proposal to replace DTL ½ waveguide blanks with shutters
  Reduces time to change operating mode of front end from ~8 hours to <20 min
  Allows RFQ to remain on with personnel in tunnel
  Reduces source restart time
  Allows more time for source R&D during maintenance days

## Slide 29: Summary
Controls is successfully
  Managing the performance of our large, distributed EPICS based control system
  Integrating a wide variety of device types
  Supporting accelerator improvement and development projects
  Improving design and development processes
  Simplifying systems to reduce support requirements and maintain availability
  Collaborating with IDAC to develop and test new software tools on the instrument beamlines before migration to the accelerator