## Slide 1: SNS Cryogenic Moderator System Operations to Support Reliability CMS Review
John Denison
Rocky Armstrong
January 22, 2020

## Slide 2: Outline
System overview
Organization structure
Best Practices
Meeting the challenges of continuing operation
Spare inventory and management processes
Summary

## Slide 3: High-level CMS operational overview
The CMS consists of two closed loop systems
  The helium refrigerator provides cooling to for 3 supercritical hydrogen loops
  Hydrogen loops provide ~20 K H2 to neutron moderator vessels housed within the Inner Reflector Plug (IRP).
An independent He loop for the hydrogen system accumulator provides backing pressure to dampen pressure transients due to beam trips
  Not discussed within this review content
High-level CMS flow schematic

## Slide 4: Cryogenic Moderator System organizational structure
The Target Operations and Maintenance Team is responsible for maintenance and operation of the CMS, along with 29 other target systems
CMS engineering resides in the Neutron Technologies Division
Research Accelerator Division
Division Director
Mechanical Systems and Operations Group
Target Operations and Maintenance Team
Target Operations
Target Support and remote handling

## Slide 5: Target Operations and Maintenance Team members
J. Denison – Team Leader
  R. Armstrong (Shift Tech., primary CMS OST SME)
  R. Ashcraft (Shift Tech.)
  L. Dial (Shift Tech.)
  M. Futrell (Shift Tech.)
  J. Moore (Shift Tech.)
  T. Russell (Shift Tech.)
  R. Wilson Jr. (Shift Tech.)
  Target Support
    D. Proveaux (Technical Manager)
    T. Crisp (Research Mechanic)
    W. Lunsford (Research Mechanic)
  Remote Handling
    L. Farr (Technical Manager)
    C. Alexander (Tech.)
    J. Clark (Tech.)
    M. McPeters (Tech.)
    D. Trotter (Tech.)
    P. Williams (Tech.)
Additional matrixed support from NTD and CMSTF

## Slide 6: Operations Shift Technician (OST) Responsibilities
OST Responsibility:
  Monitoring of 29 systems
  Daily system walk-downs
  Daily shift logs
CMS-SME OST Responsibility:
  Maintain >80% focus (R. Armstrong)
  Monitor system health (CSS and local)
  Develop input for outage planning
  Manage procurement of spares and PM materials
  P&ID management
  Procedure and training module updates
  Provide OST training
  Support other target work as directed
24/7 operational coverage from on-shift operation shift technicians as required by the Accelerator Safety Envelop (ASE)
Target Control Room (TCR)

## Slide 7: Incorporating Best Practices
Reviewed existing maintenance and operating procedures for the system
  Focused on how current practices might have contributed to CMS instability
  Compared CMS and CHL procedures for similar activities and decided on “best practice”
Determined “best practice” methodology for specific iterations
  Carbon bed processing
  System clean up
  Leak checking
  Gas analyzer configuration
  Process is ongoing
As “best practice” methodology is developed, training of personnel will follow

## Slide 8: Procedures will be systematically evaluated and updated
Long-term goal is transition to one CMS maintenance outage per year
  Reduce man-power footprint during facility outages
  Improve hardware life – reduce thermal cycles
  This requires standardization of all maintenance activities, hardware procurements, and observation of plant performance to implement industry best-practices

## Slide 9: Best-practice development will improve reliability and repeatability
Identify critical maintenance and operation activities
  Proceduralize activities and check-points
  Update and reference accurate hardware IDs
    Inclusion of valve-out configurations is critical
  Modular documentation tree to ease configuration management
    References to necessary sub-procedures
  Maintain control copy and red-line procedures
  Leverage internal expertise at the SNS CHL and HFIR Cold-source
Efforts to deploy this plan have been hindered by lack of dedicated resources
Notes: Images?

## Slide 10: CMS training modules will be updated to reflect proceduralized best-practices
Spread training module across wider period of time
Build in job-shadowing periods between classroom training modules
Require participation in critical system transitions
  Cool-down, warm-up, anomaly states
  Update to reflect current system configuration
Efforts to deploy this plan have been hindered by lack of dedicated resources

## Slide 11: Dedicated resources are required to maintain system operation and deploy a procedural update
Procedural review requires time input from SMEs
  CMSTF, CHL, HFIR, external expertise
  Technical writing support
  Review support and training
CMS technician SME is a single-point risk
  Reliable operation is aided by procedural/training updates, but personnel availability remains a concern

## Slide 12: Carbon loading and processing procedures were updated
Diagnostics are built into processes to best suit the current state of the system
Drying process now cycles between heated nitrogen flow, isolation, and cold-trapping exhaust to diagnose volume purity
  Provides method of ensuring dryness and removing nitrogen from isolated CB volumes
Carbon addition technique was improved
  Screened drum and vacuum assembly to remove particulate as carbon is added
  Prevents migration of carbon particulate downstream
  Prevents potential increase of DP and loss of capacity
Carbon sifting on screened-drum

## Slide 13: Purging routine has been enhanced
System recovery following exposure to atmosphere
  Standardized methods
  Leverage experience at CHL to improve repeatability
  Isolate and vary heated N2 flow paths to remove moisture and limit effected volume
    Deploy cryo-trapping in purge exhaust as diagnostic
  He purge to pressure, 30-min hold period, cold-trap exhaust
  Purge with He flow through the He purification system when possible
  Minimize volume of system opened to atmosphere during maintenance activities
  Increase number of purge/backfill cycles
Clean cryo trap from HX header
Cryo trap with moisture pumped from carbon vessel

## Slide 14: He purification capabilities returned to service
80 K liquid nitrogen purification system
  60 g/s capacity, slip-stream function
  Requires main compressor for motive force
Developed piping and valve lineups to permit purification of isolated system volumes
  Permits purification of large portions of the system while invasive activities continue elsewhere
  Identified and included provisions to ensure purifications of system dead-legs
Typical minimum system purification period of 4 days

## Slide 15: CMS He contamination monitoring improvements
Additional LGA sampling ports added to permit contamination monitoring elsewhere in the system
  Investigation of individual component performance during summer 2019 transient behavior
Identified incorrect discharge conditions
  Short-term solution is inefficient
  He waste limits sampling to every other week
CHL collaboration has improved and standardized operational practices
  Purge of pyrolizer conducted prior to powering on unit
  Improves purity of sampling window
Routine calibration now standard
Dew-point readings included as standard procedure in purging operations
Linde picture and dew point meter picture picture

## Slide 16: Leak checking processes have been standardized and widely deployed
Engage SNS vacuum group for support
  Leverage expertise
  Dedicated resource
  Collaboration has improved OST leak checking skillset
Increased frequency of routine, blanket leak checks
  Expanded scope of routine checks to include compressor building, ORS, cold box, and HUR

## Slide 17: Meet the challenges that continue to arise
Heater Margin
Beam Power
January 8, 2020
Failed heater fuse lead to development of a procedure to safely replace while running cold with beam on target
January 9, 2020
Fuse Failure
Fuse Replacement

## Slide 18: Spares inventory and management processes have improved
Aggressive outage schedules have forced improvements to this process
  Consolidation of tracking to single system
  Procurement process has been a bottleneck
    Vendor performance remains an issue
    Management consumes OST resource
    Quick response to incoming data requires lean system

## Slide 19: Summary of charges
  Is the plan to return the CMS to reliable operation for 1.4 MW beam power by April 2020 reasonable? Are there additional considerations that need to be included?
    Maintenance activities are being executed in compliance with industry best-practices to support reliable operation at 1.4 MW beam power. CMS operational performance in the Winter 2019-2020 SNS run-cycle is promising.
  Is the plan to prepare the CMS for reliable operation for the beam power ramp up defined for the PPU culminating in 2.0 MW beam power in Q3 2024 reasonable? Are there additional considerations that need to be included?
    The CMS is currently maintaining stable operation with enough capacity to support 2.0 MW beam on target. Additional gains in capacity and long-term delivery of reliable operation at both 1.4 MW and 2.0 MW beam power will be supported by the deployment of a plan to standardize CMS maintenance activities.
  Are the allocated resources sufficient to execute the CMS plans? Is the organization structure for CMS resources reasonable to carry out the scope of work defined in the operations plans?
    Added resources to support standardization and update of procedural documentation to reflect best-practices would be beneficial.