## Slide 1: USI Evaluations Since Last Assessment – ASRC 2016
Presented to the
Accelerator Safety Review
Committee
J. Platfoot, Nuclear Facility Safety Engineer
Nuclear and Radiological Protection Division
July 26, 2016

## Slide 2: USI Evaluations conducted at SNS
97 USI Evaluations conducted to date (March 2004 – present)
17 USI Evaluations since last ASRC Review (June 2013)
2 Positive USI Evaluations to date
  Neutron scattering with Pu Samples (June 2012)
  PPS common mode failure (August 2013)

## Slide 3: USI Evaluations since Last Assessment Personnel Protection System
Common Mode Failure
  PPS redundant 24V power supply common mode failure (Aug 2013)
  PPS power supply wiring modifications and watchdog diagnostics (Dec 2013)
  Replacement of CCR PPS rack cabinets 03, 04, 05, and 06 (Jul 15)
  Isolate power supply commons in klystron gallery (Jan 2016)
  Isolate power supply commons in HEBT (Apr 2016)
Removal of non-credited magnet electrical safety interlocks (Jan 2016)
Modification of TPPS to resolve primary shutter reopening abnormality (Jul 2015)
Lack of HEBT chipmunk logic functionality check in PPS certification (Aug 2013)

## Slide 4: USI Evaluations Since Last Assessment Target Systems
Target Evaluation
  Interim storage of spent target modules with target building (Mar 2015)
  Addition of diagnostic instruments into target interstitial (Mar 2015)
  Addition of generation II diagnostics into target interstitial (Nov 2015)
Evaluation of core vessel insert leak (Jul 2013)
Replacement of worn components in water mist system (Jul 2014)

## Slide 5: Others
Beam Lines / IPPS
  BL 1A USANS low power alignment testing (Feb 2014)
  BL 16B VISION secondary shutter deceleration switches (Feb 2014)
  BL 11 and BL 1 primary shutter control logic (Jun 2014)
CHL cryogenic test facility helium dewar system (Jul 2013)