## Slide 1
DOE/SC Independent Project Review of the Proton Power Upgrade Project
Erica Ahlschwede
Level 3 Manager for Target Utility Systems
September 14-17, 2021
P.5.6 Target Utility Systems

## Slide 2: Outline
Scope
Organization
Progress since CD-2/3
Challenges
Final design status
Installation plans
Cost and schedule
Labor profile
Risk register
Responses to recommendations
ESH&Q and COVID-19 impacts
12-month look-ahead
Summary

## Slide 3: Scope
P.5.6.1: Management & System Integration
P.5.6.2/.3: Evaluations/Upgrades for increased beam energy from 1.0 to 1.3 GeV @ 2MW – Complete prior to CD-2/3
    4 Primary Target Cooling Water Loops
    4 Secondary Cooling Water Loops
    3 Tertiary Cooling Water Loops
    Nitrogen and Helium Gas Distribution
P.5.6.4: PPU Upgrades for Gas Injection for 1.3 GeV @ 2MW
  Electrical Upgrade in target building basement
  Recirculating gas injection systems
    Target bubblers (up to10 slpm; PPU)
    Target wall (up to 10 slpm; PPU)
  “Once-through” helium (as backup to recirculating system)
    Target bubblers (up to10 slpm via Gas Panel 9 provided by Operational Upgrades/Not PPU)
    Target wall (up to 10 slpm via Gas Panel 10; PPU)
  Molecular sieve system
Charge: 1

## Slide 4: Organization
Charge: 5

## Slide 5: Progress since CD-2/3
12-month look-ahead from CD-2/3
Complete supporting analyses and design on outstanding gas injection upgrades (equipment, molecular sieve systems and electrical upgrades)
Start procurement of components
Off-normal Analysis for FTS system upgrades
May 2021 – Final Electrical Design review
Charge: 1

## Slide 6: Progress since CD-2/3
Off-normal Analysis for FTS system upgrades
  Complete Oct 2020
Molecular Sieve PDR (P.5.6 and P.5.8)
  Complete Oct 2020
  Design continues to progress
Basement electrical upgrade FDR
  Complete Feb 2021
Temperature control valve TCV-1061 received
  March 2021
Gas Panel 10 FDR
  Complete May 2021
Compressors for gas recirculation received
  June 2021
Charge: 1
B2-8 Stephens
B2-8 Stephens, B2-10 Platfoot, B2-5 Edwards

## Slide 7: Progress since CD-2/3
Off-normal Analysis for FTS system upgrades
  9 action items
    6 closed
Basement Electrical Upgrade
  Procurement started April 2021
  Installation began June 2021
    Building 8700 power outage to allow for electrical tie into transformer occurred June 2021
  Installation expected to be complete fall 2021
Charge: 1, 2
New electrical cables from floor above
New electrical panel in 8700 Basement

## Slide 8: Progress since CD-2/3
Gas Recirculation
  Received 4 Compressors
    Long lead item from Germany
    Received June 2021
  Created hydraulic model of Hg loop, to help identify pressure drop concerns and issues
  Identified the need for make up He to compressor suction during start-up
  HVAC engineering design for ‘snorkel’ to capture potential He leaks from compressor diaphragm
Charge: 1, 2

## Slide 9: Overview of Gas Flow Path
Green: Mol Sieves
Magenta: PPU Delay Bed
Blue: Gas recirculation compressors
Red: Transfer lines run through GAR, CAR, and MOTS
Gas travels through CuO reactor, MOTS Mol Sieve, and finally the cold trap
Charge: 1
Gas recirculation line to high bay
GAR
CAR
MOTS

## Slide 10
Progress since CD-2/3
Gas Recirculation equipment layout
  Red: compressors
  Yellow pipe: snorkel system
Charge: 1
Target wall train

## Slide 11: Progress since CD-2/3
Molecular Sieve Design (P.5.6 & P.5.8)
  Tritium samples of existing mol sieves were taken in Nov 2020
    Quantify tritium production and document findings
    Sample results received week of August 13th
  Met with radiation safety committee in Jan 2021, with RSC concerns around the high dose rates in the GAR
    Team tasked to identify solutions to help remediate
  Discovered the clam shell style shielding design concept was not viable
    Unable to find a high temperature (600 F) and high radiation paint application
    Team transitioned to a steel lined shielding design currently in use on the gold bed
  Design team underwent the task of re-evaluating the vessel size, to reduce source term values
    Received Ops management buy in for smaller vessel size
    Determined that a 5th vessel for regeneration is not required
Charge: 1
B2-8 Stephens

## Slide 12: Progress since CD-2/3
Molecular Sieve Design
  Comparison “old” vs “new”
  Old: 6” diameter vessel with clam shell style lead brick shielding
  New: 3” diameter vessel with SS lined, poured lead design shielding
    Smaller vessels reduce source term by ~50% with the same shielding thickness
Charge: 1
6” diameter with lead brick shielding
3” diameter with SS lined, poured lead shielding
B2-8 Stephens

## Slide 13: Progress since CD-2/3
Molecular Sieve Design (P.5.6 & P.5.8)
  Detailed discussions held with mol sieve vendors to communicate complexity of project
    3 potential vendors are engaged, and feel comfortable with the project
  Source term DAC revision
    To address design progression and correct delay time
  On / off valve selection complete
    He leak tight, high temperature and high radiation application, need to fit into a small space
  Met with RSC to present new source term findings (June 2021)
    RSC recommends approval of new shielding design
Charge: 1
B2-8 Stephens

## Slide 14: Progress since CD-2/3
Mol sieve equipment layouts
  Red: system in GAR
  Green: system in MOTS
Charge: 1
Gold Amalgamation Room (GAR)
MOTS
B2-8 Stephens

## Slide 15: Progress since CD-2/3
Mol sieve equipment layouts - GAR
Charge: 1

## Slide 16: Progress since CD-2/3
Mol sieve equipment layouts - MOTS
Charge: 1
B2-8 Stephens

## Slide 17: Challenges
Technical
  Mercury Loop Recovery Event (MLR)
    Event occurred March 2019, project completed Dec 2020
  Source term generation
    Evaluated for each piece of equipment, under different flow rates and different flow configurations
    RSC request to mitigate high source term values
  Gas recirculation flow configurations
    Once through, two different options to ‘recycle’
    Hydraulic model identified need for helium introduction into compressor suction for pressure profile and to maintain helium purity
  Mol sieve design complexity
    600 F temps, high radiation, He service, small installation footprint, low dewpoint required, little to no pressure drop required
    On / Off Valve selection
    Process instrumentation must survive the same environment
    Shielding design
Charge: 1
B2-8 Stephens, B2-10 Platfoot, B2-5 Edwards

## Slide 18: Challenges
Technical
  Internal Resources moved to STS
    Process design engineer
    3D designer
  Coordination of Subcontract Support
    Process engineering - flow sheet development and hydraulic modeling (was part time; now full time)
    Nuclear HVAC engineering design (part time)
    3D modeling and designer (was part time; now full time)
    Seismic/Structural engineering design (part time)
    Process Controls engineering design – instrumentation selection (part time)
  FTS Operations Support
    Ion exchange column deuteration
    Procurement of heavy water
    RID water chemistry support
    Recombination & Recycle
    Beamline support
Charge: 1

## Slide 19: Challenges
Schedule
  Nature of the technical challenges negatively impacted design schedule
  At CD-2/3, Mol Sieve FDR was projected to occur in March 2021
    FDR will occur later than schedule shows, in the fall of 2021
  Mol Sieve mechanical installation projected to occur during the long outage in FY23
Procurement
  Mol sieve equipment specification
    Will be tricky to write
    Accurate communication of the technical challenges is key to success
Charge: 1, 4

## Slide 20: Final Design Status
Two areas are not yet at final design
  Gas Recirculation: 90%
  Molecular Sieves: 90%
Technical issues have been addressed
Supporting documentation and drawing packages need to be completed
FDR anticipated Fall 2021
  Gas recirc install expected to begin winter 2021
    No risks anticipated with completing final design
  Mol sieve install expected in the extended outage in FY23
    Ensuring accurate equipment specification
Charge: 1

## Slide 21: Installation Plans
Electrical Upgrade: May 2021 – Fall 2021 Gas Panel 10: Sept 2021 – Nov 2021
Gas Recirculation: Dec 2021 – Sept 2022 Mol Sieve: Feb 2023 – May 2023
Charge: 4

## Slide 22: Cost and Schedule
Charge: 4
Chart: P.05.06 - Target Utility Systems
| FY2021 | FY2022 | FY2023 | FY2024 | FY2025
Actual Cost Oct - May FY21 | 629.8869
Labor | 321.3371 | 477.7028 | 147.6015 | 0 | 0
Material | 258.6446 | 892.734 | 33.9994 | 0 | 0

## Slide 23: Cost and Schedule
Charge: 4

## Slide 24: Labor Profile
Charge: 4, 5

## Slide 25: P.05.06 Risk Register
No active risks identified
  Two risks retired
High Risks
  No high risks identified
Key risk categories analyzed
  Scope uncertainty
Risks are reviewed on a regular basis
Charge: 1

## Slide 26: Responses to Recommendations
No recommendations from the CD-2/3 review
Recommendations from prior DOE reviews are closed
Charge: 6

## Slide 27: ESH&Q and COVID-19 Impacts
ESH&Q Impacts
  None
COVID-19 Impacts
  Difficulty with technical reviews (Off Normal and Mol Sieve PDR)
    Keeping folks engaged for the duration of the technical meeting
  KNF Compressors for Gas Recirculation
    Encountered a 2-month delay
      Expected arrival in 4 months, received after 6 months
      No impact to installation schedule
Charge: 3

## Slide 28: 12-Month Look-Ahead
Complete mol sieve and gas recirculation final designs
  Host FDR
Electrical upgrade installation complete
Gas Panel 10 mechanical installation complete
Gas Recirculation mechanical installation near completion
Mol sieve procurement process near completion
Charge: 1, 4

## Slide 29: Summary
Completed HAZOP
Molecular Sieve Design Progress (P.5.6 and P.5.8)
  Addressed numerous technical challenges
  FDR expected Fall 2021
Basement electrical upgrade installation
Gas Panel 10 installation
Gas Recirculation design progress
  FDR expected Fall 2021
Project Team has overcome multiple challenges and has completed a substantial amount of work
  Thank you for your time!
Charge: 1