## Slide 1
DOE/SC Independent Project Review of the Proton Power Upgrade Project
Greg Norman
Level 3 Manager for RF System Utilities
September 14-17, 2021
P.03.07 RF System Utilities

## Slide 2: Outline
Scope
Organization
Progress since CD 2/3
Challenges
Final design status
Installation plans
Cost and schedule
Labor profile
Risk register
Responses to recommendations
ESH&Q and COVID-19 impacts
12-month look-ahead
Summary

## Slide 3: Scope
P.3.7 RF Utilities
  P.3.7.1 Management and system integration
  P.3.7.2 New SCL DI Water Cooling System (KL-06)
  P.3.7.3 Upgrade existing DTL DI Water RF Cooling System (KL-04)
  P.3.7.7 New SCL RF Electrical Utilities
Charge: 1

## Slide 4: Scope
  P.3.7.2 New SCL RF Cooling System (KL-06)
    New KL-06 SCL DI water cooling system will be provided to cool the 28 new SCL klystrons, the associated RF equipment, and 3 HVCM’s to be added to the klystron gallery
    The 3.7.2 WBS scope includes the following:
      Design the new pump room and DI water distribution system - complete
      Purchase Pump room major equipment (pumps & heat exchanger) - complete
      Provide RF equipment piping tie-in’s
Charge: 1
PUMP ROOM
HVCM
KLYSTRONS
TRCC
XMTR 25 AREA
XMTR 27 AREA
XMTR 28 AREA
XMTR 30 AREA
XMTR 31 AREA

## Slide 5: Scope
  P.3.7.2 New SCL RF Cooling System (KL-06) – cont.
    KL-06 system construction scope is under conventional facilities WBS P10.6.2.1
      Construction was completed April 2021
Charge: 1
B5-2 Santee

## Slide 6: Scope
  P.3.7.3 Modify DTL & FEB RF Cooling System (KL-04)
    Modify existing KL-04 DTL & FEB DI water cooling system to meet increased loads from the new 3.0 MW klystrons being added. The pumps are already overloaded with existing equipment requirements. The project will increase the size of the two DI water cooling pumps, and all associated electrical feed equipment
    Provide the new DI water cooling tie in piping for the 3.0 MW Klystrons
Charge: 1
KL-04 DI Water Pumps
Klystron Piping

## Slide 7: Scope
  P.3.7.7 SCL RF Electrical Utilities
    The WBS 3.7.7 scope:
      Provide all technical equipment racks
      Provide electrical service cables to technical equipment racks and systems from the AC distribution panels (Interface is the circuit breaker)
      Provide all control cabling from technical equipment racks to the equipment, including the cryomodules in the LINAC
      Provide grounding plane for all technical equipment
      Install all waveguides, circulators, and loads
    Conventional facilities CD 3B scope:
      Provide the primary AC distribution equipment including all power panels and transformers - complete
      Provide all primary raceway such as the main wire-way and cable-tray for all cable types - complete
      Provide the 80kVA UPS and distribution panel - complete
Charge: 1
B5-2 Santee

## Slide 8
P.3 – RF Systems
John Moss
P.3.7 Utilities
Greg Norman
P.3.3 NCL HPRF
John Moss
P.3.2 SCL HPRF
John Moss
P.3.8 RF Controls Karen White
P.3.6 New Linac
Modulators
David Anderson
P.3.4 LLRF
Mark Crofford
P.3.1
Management and System Integration John Moss
P.3.9 Global Controls Karen White
P.3.5 Existing Linac
Modulators
Chris Pappas
P.3.1.1
Management and System Integration
John Moss
P.3.2.5 Circulators
John Moss
P.3.2.3 Klystrons
John Moss
P.3.2.2
Transmitters
John Moss
P.3.2.1
Management and System Integration
John Moss
P.3.3.3 Klystrons
John Moss
P.3.3.4 Circulators
Sung-Woo Lee
P.3.3.2
Transmitters
John Moss
P.3.3.5 Glycol/ Water Loads Sung-Woo Lee
P.3.3.1
Management and System Integration
John Moss
P.3.4.2 LLRF System
Mark Crofford
P.3.4.3 Arc Detectors
Mark Crofford
P.3.4.1
Management and System Integration
Mark Crofford
P.3.4.4 Reference Line
Chip Piller
P.3.5.2 Modulator System
Chris Pappas
P.3.5.3 Modulator Control System Mark Wezensky
P.3.5.1
Management and System Integration
Chris Pappas
P.3.5.4 Modulator SystemTest
Article
Chris Pappas
P.3.6.3 SCR System
David Anderson
P.3.6.4 Modulator System
David Anderson
P.3.6.2
Transformer
David Anderson
P.3.6.5 Modulator Control System Mark Wezensky
P.3.6.1
Management and System Integration
David Anderson
P.3.6.6 Integrated System
David Anderson
P.3.7.3 Water Utilites, Modify
Existing RFQ/DTL
Greg Norman
P.3.7.2 Water Utilities, New Cold
Linac SCL RF
Greg Norman
P.3.7.7 Electrical
Greg Norman
P.3.7.1
Management and System Integration
Greg Norman
P.3.8.2 Linac RF Controls
Alan Justice
P.3.8.3 Linac Water System
Controls
Derrick Williams
P.3.8.1
Management and System Integration
Alan Justice
P.3.9.2 Linac/SCL Timing/MPS Alan Justice
P.3.9.3 Linac/SCL Protection System
Kelly Mahoney
P.3.9.1
Management and System Integration
Alan Justice
P.3.9.4 Linac/SCL Networking and
Computing
Alan Justice
P.3.5.5 Warm Linac Test HVCM
Chris Pappas
P.3.5.6 Upgrade RFQ-Mod1 Chris Pappas
Charge: 5
Organization
John Kristy
(Installation Coordinator)
William Barnett
(Electrical SME)
David Carlson
(Elect. Installation Coord.)

## Slide 9: Progress since CD 2/3
P.3.7.2 New KL-06 SCL DI Water Cooling System
  CD 2/3 12 Month Look-Ahead
    “Construction is scheduled to be completed in January 2021 (CD 3B scope), except for piping tie ins to the RF equipment after it is installed later in 2021/2022”
  Progress:
    Construction was completed in April 2021 for the Klystron Gallery Bldg. SCL expansion which included the KL-06 pump room, equipment, instruments, and all piping
    The KL-06 DI water cooling system pump room equipment and instruments have been fully tested, and controls programming has been completed and tested
    Remaining work includes installation of the RF Transmitter Cooling Carts (TRCC) and water connections to the RF Equipment once installed in the Klystron Gallery
    KL-06 Commissioning Completion Milestone date is April 2023
Charge: 1,2

## Slide 10: Progress since CD 2/3
  P.3.7.4 Modify KL-04 DTL DI Water Cooling System
  CD-2/3 12 Month Look-Ahead
    “All design and construction documents are complete and approved and ready for start of construction in June 2021”
  Progress:
    Construction was moved back to Oct-21 (Outage FY22A)after a more fully developed installation schedule showed more outage days were required
    The new pumps, motors, and Variable Frequency Drives are on order and scheduled to be received in September 2021
    The installation contract has been awarded
Charge: 1,2

## Slide 11: Progress since CD 2/3
  P.3.7.7 Klystron Gallery SCL Electrical Utilities
  CD-2/3 12 Month Look-Ahead
    “Remainder of cable, racks, and hardware necessary for completion of PHASE 1 (CM31 & CM32) will be purchased and received and the PHASE 1 installation will begin”
  Progress:
    All cable, racks, and hardware for Phase 1 installation have been purchased. All have been received with the following exceptions:
        CRYO Marshalling, Tuner and CRYO Control racks [Obsolescence of specified components]
        ~ ½ the vacuum connectors. Beam Line and Insulating [Availability]
        Specialized cables delivery has been delayed [Availability]
    Installation of the ground plane for the racks and equipment involved with Phase 1 is underway
    All racks that have been received for Phase 1 are installed
    Waterfall cable tray to technical racks is complete for rack rows 53,52,51 and 50
    2100 VAC OKONITE cable pulls from PPU Substations to corresponding HVCM SCR locations are complete
    13.8 KV AC feeds to the PPU substations are complete
    Cable pull lists for the October Outage are complete for LLRF, CRYO and Beam Line & Insulating Vacuum Systems
    Cable pulls for AC service to rack rows 53, 52, 51, 50 and 49 is underway
Charge: 1,2

## Slide 12: Progress since CD 2/3
16% of the scheduled work has been completed with an increase of $613K in BAC since CD 2/3
Charge: 4

## Slide 13: Project Change Requests since CD 2/3
Charge: 4

## Slide 14: Challenges
P.3.7.2 New KL-06 SCL DI Water Cooling System
  No current challenges
  P.3.7.4 Modify KL-04 DTL DI Water Cooling System
  No current challenges
Charge: 1,2

## Slide 15: Challenges (cont)
  P.3.7.7 Klystron Gallery SCL Electrical Utilities
  Late completion of Klystron Gallery SCL area construction delayed the utilities installation start date
  Availability of Davis-Bacon craft personnel is compromised
  Technical equipment delivery delays
  Availability or obsolescence of specified parts, [cable, connectors, system components
    A PCR was processed in June which has updated the baseline based on all of the above
Charge: 1,2

## Slide 16: Final Design Status
All RF Utilities Final Design Reviews are complete with no outstanding recommendations
Charge: 6

## Slide 17: Installation Plans - DI Water Systems
Remaining KL-06 DI Cooling System installation of TRCC carts and final connections to RF equipment is not outage dependent
  3 Phase approach
    Phase 1 – Install TRCC carts 30 & 31, cooling connections to SCR/HVCM 30, and cooling connections to the 1st 10 Klystrons, Circulators and RF Loads
    Phase 2 – Install TRCC carts 27 & 28, cooling connections to SCR/HVCM 28, and cooling connections to the 2nd set of 10 Klystrons, Circulators, and RF Loads
    Phase 3 – Install TRCC cart 25, cooling connections to SCR/HVCM 25, and cooling connections to the 3rd set of 8 Klystrons, Circulators, and RF Loads
      KL-04 DI Cooling Pump Upgrades are scheduled to be completed during Outage FY22A in October 2021
Charge: 4,5

## Slide 18: Installation Plans – SCL RF Electrical Utilities
SCL Electrical Utilities installation occurs in 3 phases
    Phase 1 Activities (Klystron Gallery – non outage work)
      Transmitter 30 & 31 racks and all associated racks, 10 klystron tanks, and TRCC carts, SCR/HVCM 30 and 1st 10 Klystrons. All cable tray, ground plane, wiring, and terminations for the above. Waveguide, RF Circulators, and RF Loads
    Phase 1 Activities (LINAC – outage work)
      All Phase 1 cables from the KG to the LINAC and terminations [CM32 & 31]
    Phase 2 Activities (Klystron Gallery – non outage work)
      Transmitter 27 & 28 racks and all associated racks, 10 klystron tanks, and TRCC carts, SCR/HVCM 28 and 2nd 10 Klystrons. All cable tray, ground plane, wiring, and terminations for the above. Waveguide, RF Circulators, and RF Loads
    Phase 2 Activities (LINAC – outage work)
      All Phase 2 cables from the KG to the LINAC and terminations [CM30, 29, & 28]
    Phase 3 Activities (Klystron Gallery – non outage work)
      Transmitter 25 racks and all associated racks, 8 klystron tanks, and TRCC carts, SCR/HVCM 25 and final 8 Klystrons. All cable tray, ground plane, wiring, and terminations for the above. Waveguide, RF Circulators, and RF Loads
    Phase 3 Activities (LINAC – outage work)
      All Phase 3 cables from the KG to the LINAC and terminations [CM27 & 25]
Charge: 4,5

## Slide 19: Installation Layout by Phase – RF Electrical Utilities
PHASE 3
PHASE 2
PHASE 1

## Slide 20
long outage
FY18
FY19
FY20
FY21
FY22
FY23
FY24
FY25
FY26
CD-4
(E)
CD-4
(L)
42 months contingency
FY27
FY28
CD
3B
CD
2/3
CD
1
CD
3A
RF Systems Preliminary Design Complete
RF Systems FD Complete (Excl. LLRF & RFQ-DTL HVCM)
RF Systems FD Complete (LLRF & RFQ-DTL HVCM)
Procure/Fab RF Systems Controls
Transmitter Design & Fab First Article
Procure/Fab Transmitters
Procure/Fab SCL Klystrons
First High-Power Test for XMTR 30 & 31 (8/2022), 27 & 28 (11/2022), and 25 (11/2023) Complete
Procure/Fab WG, Circs and Loads
Procure/Fab Transformers & SCR
Procure/Fab New Modulator Systems
Proc/Fab LLRF
Proc/Fab Upg. Linac Modulators
Procure/Fab 3MW Klystrons
3MW Klystron Design & Fab First Article
Procure/Fab Utilities/Electrical
Existing Linac – Test HVCM w. Dual 3.0 MW Klystrons
RF SCL Installation
RF Summary Schedule Editable Diagram
Charge: 4

## Slide 21: Budget and Estimate to Complete
Charge: 4
We are 29% complete in RF Utilities (Design’s and major procurements)
Installation is remaining

## Slide 22: Cost Estimate by FY
Chart: P.03.07 Utilities
| FY2021 | FY2022 | FY2023 | FY2024 | FY2025
Actual Cost Oct - May FY21 | 952.8555
Labor | 1078.0063 | 2003.4172 | 404.2423 | 102.1248 | 0
Material | 1006.2735 | 587.6784 | 1.5233 | 29.3888 | 0
Charge: 4
- Labor is mostly Davis-Bacon Craft (Electrical Utilities)
- FY21/22 materials are primarily the receipt of Phase 2 & 3 electrical items

## Slide 23: Labor Profile
The majority of the labor is for RF Electrical Utilities Installation
  June PCR changes this distribution
Charge: 4

## Slide 24: P.03.07 Utilities Risk Register
Two active risks identified
  No risks retired
  Pre-mitigated ranking: 2 Medium
  Post-mitigated ranking: 1 Low, 1 Medium
High Risks
  No high risks identified
Key risk categories analyzed
  Vendor skill
  Craft availability
Risks are reviewed on a regular basis
Risk ID | L3 WBS | Risk Title | Expiration Date | Mitigation | Pre-Mitigation Rank | Post Mitigation Rank
T-P.3-031 | P.03.07 | Availability of Davis-Bacon craft personnel is compromised | 10/1/2021 | Work with the PPU installation coordinator, who also manages the GEM Technologies contract, to ensure needed craft resources are available when needed. Consider premium payments and/or overtime to compete with other local projects, e.g., UPF | 6 | 6
T-P.3-030 | P.03.07 | Installation does not match 3D model | 9/1/2022 | Ensure adequate Quality Controls Oversight | 6 | 2
T-P.3-031 mitigation:
Utilizing internal resources to supplement D-B craft
Retaining Electrical SME
Schedule has been adjusted to redistribute the manpower.
Charge: 5

## Slide 25: Responses to Recommendations
No recommendations from the CD 2/3 review
Recommendations from prior DOE reviews are closed
Charge: 6

## Slide 26: ESH&Q and COVID-19 Impacts
ESH&Q impacts
  One procurement non-conformance: KL-06 pump motor amps are higher than the manufacturers published values
COVID-19 impacts
    Quarantines during CF construction (5 weeks)
    Technical equipment fabrication and delivery delays
Charge: 3,5

## Slide 27: 12-Month Look-Ahead
Charge: 4,5
P.3.7.2 KL-06 SCL DI Water Cooling System
  Install TRCC carts 30 & 31, cooling connections to SCR/HVCM 30, and cooling connections to the 1st 10 Klystrons, Circulators and RF Loads
      Phase 1 Piping Complete in April 2022
  Install TRCC carts 27 & 28, cooling connections to SCR/HVCM 28, and cooling connections to the 2nd 10 Klystrons, Circulators and RF Loads
      Phase 2 Piping Complete in August 2022
  Phase 1 1st High Power Test (Xmtr 30&31) in July 2022
  P.3.7.4 Modify KL-04 DTL DI Water Cooling System
  Receive pumps and VFD’s in September 2021
  Installation is scheduled to be completed during Outage FY22A (October 2021)

## Slide 28: 12-Month Look-Ahead
Charge: 4,5
  P.3.7.7 Klystron Gallery SCL Electrical Utilities
    Phase 1 Activities (Klystron Gallery – non outage work)
      Transmitter 30 & 31 racks and all associated racks, klystron tanks, and TRCC carts, SCR/HVCM 30 and 1st 10 Klystrons. All cable tray, ground plane, wiring, and terminations for the above. Waveguide, RF Circulators, and RF Loads
    Phase 1 Activities (LINAC – outage work)
      All Phase 1 cables from the KG to the LINAC [Outage FY22A – October 2021]
      Terminate all Phase 1 cables in the LINAC [Outage FY22B – March 2022]
    1st High Power Test (Phase 1 - Xmtr 30&31) in July 2022
    Phase 2 Activities (Klystron Gallery – non outage work)
      Transmitter 27 & 28 racks and all associated racks, klystron tanks, and TRCC carts, SCR/HVCM 28 and 2nd 10 Klystrons. All cable tray, ground plane, wiring, and terminations for the above. Waveguide, RF Circulators, and RF Loads
      Note: Dates shown are based on the PCR processed in June 2021

## Slide 29: Summary
All designs and FDRs are complete for the Klystron Gallery RF Utilities WBS’s
There are no outstanding recommendations from previous reviews
The KL-06 SCL DI Water Cooling System equipment, instrument, and piping installation has been completed and fully tested, and the tie ins to the RF equipment and HVCM’s are on schedule and will occur for Phase 1 & 2 in the next 12 months
The KL-04 DTL DI Water System modifications are scheduled for October 2021 [Outage FY22A]
The SCL RF Electrical Utilities installation ramped up slower than scheduled but has now recovered
  Risk # T-P.3-031 “Availability of Davis-Bacon craft personnel is compromised” was realized
  PCR to modify schedule dates was approved in June, before any large variances ocurred
  Detailed planning and installation coordination is ongoing so installation efficiency should improve over time and result in schedule benefits to offset some of the slip from initial manpower limitations