## Slide 1
DOE/SC Independent Project Review of the Proton Power Upgrade Project
Greg Norman
Level 3 Manager for Ring Systems - Utilities September 14-17, 2021
P.04.05 Ring Systems - Utilities

## Slide 2: Outline
Scope
Organization
Progress since CD 2/3
Challenges
Final design status
Installation plans
Cost and schedule
Labor profile
Risk register
Responses to recommendations
ESH&Q and COVID-19 impacts
12-month look-ahead
Summary

## Slide 3: Scope
P.4.5 Ring Utilities
  P.4.5.1 Management and System Integration
  P.4.5.2 Main Ring Dipole Transformer Cooling Upgrade
  P.4.5.3 RN-03 Magnet Power Supply DI Cooling Water Upgrade
  P.4.5.4 PFN Room HVAC
Charge: 1

## Slide 4: Scope
P.4.5.2 Main Ring Dipole Transformer Cooling Upgrade
Charge: 1
Add transformer cooling fan kits to existing 1500 kVa (4681 amp) transformers to increase capacity to 1725 kVa (5384 amps)
2 Cooling Fans per Transformer (Typical)

## Slide 5: Scope
P.4.5.3 RN-03 Magnet Power Supply DI Water Cooling Upgrade
Charge: 1
Replace the 3 existing smaller capacity pumps with 2 larger pumps (1 installed spare)
  Goulds 3196 (475 GPM @ 230 FT)
Add additional heat transfer area (plates) to the existing heat exchanger and change cooling media from Tower Water to Chilled Water
  Alfa Laval M10-BFG (550 kW/h)
  Decommission existing RF Power Supply chilled water trim cooler on the main floor
  Install Water Chemistry Panel and Flow Control Valve to automate system resistivity control
  Add instrumentation for improved system monitoring and control

## Slide 6: Scope
P.4.5.4 PFN Room HVAC
Charge: 1
Install two Liebert Mini-Mate air handling units suspended from the roof structure; 12 tons total capacity (72 F @ 50-55% RH)
Utilize existing facility Chilled Water and Heating Water Systems
Humidification and dehumidification control
BACnet compatibility for controls connection to EPICS
Supply ductwork along the center of the room with air distribution grilles
Remove existing roof-mounted fans and use those penetrations for outside air intake Remove, seal and insulate the existing wall-mounted filter louver intake openings and seal the partition wall at the roof deck

## Slide 7
P.4 Ring
Nick Evans
P.4.2 Injection Region
Robert Saethre
P.4.7 RTBT Stub
Nick Evans
P.4.6 Ring Control Systems Karen White
P.4.3 Injection Dump
Charlotte Barbier
P.4.1
Management and System Integration Nick Evans
P.4.8
Accelerator Physics Nick Evans
P.4.5 Utilities
Greg Norman
P.4.4
Extraction Region Robert Saethre
P.4.1.1
Management and System Integration
Nick Evans
P.4.3.1
Management and System Integration
Dave Willis
P.4.4.3 Power Supplies
Robert Saethre
P.4.4.2 Magnets
Robert Saethre
P.4.4.1
Management and System Integration Robert Saethre
P.4.5.2 Main Ring Dipole XFMR
Upgrade
Greg Norman
P.4.5.3 RN-03 DIW
Cooling Upgrade
Greg Norman
P.4.5.1
Management and System Integration
Greg Norman
P.4.6.3 Personnel Protection System
Kelly Mahoney
P.4.6.4 Ring Injection Section
Controls
Derrick Williams
P.4.6.2 Beam Power Limit
Systems
Patrick Bong
P.4.6.5 Ring Extraction Section
Controls
Derrick Williams
P.4.6.1
Management and System Integration Derrick Williams
P.4.7.2 RTBT Stub Temporary Shielding
Nick Evans
P.4.7.3 RTBT Stub Earth Berm Shielding
Nick Evans
P.4.8.1 Accelerator Physics
Nick Evans
P.4.5.4
PFN Room HVAC
Greg Norman
P.4.3.2 Injection Dump Imaging
Dave Willis
P.4.3.3 Injection
Dump Engineering
Review
Melissa Harvey
P.4.1.2
Design
Nick Evans
P.4.2.1
Management and System Integration Robert Saethre
P.4.2.2 Magnets
Robert Saethre
P.4.2.3 Power Supplies
Robert Saethre
P.4.2.4 Vacuum Systems
Charlotte Barbier
P.4.2.5 Primary and Secondary
Stripper Foil
Charlotte Barbier
Charge: 5

## Slide 8: Progress since CD 2/3
P.4.5.2 Main Ring Dipole Transformer Upgrade
  Main Ring Dipole Transformer Fan kits have been ordered
  Installation scheduled for October 21 (Outage FY22A)
P.4.5.3 RN-03 Magnet Power Supply DI Cooling Water Upgrade
  FDR was completed and there are no open recommendations
  P.4.5.4 PFN Room HVAC
  FDR was completed and there are no open recommendations
Charge: 1,2

## Slide 9: Progress since CD-2/3
Charge: 4
Ring Utilities is 25% complete with only a slight increase (+$25K) in the BAC since CD 2/3

## Slide 10: Project Change Requests since CD 2/3
Charge: 4
Ring Utilities = $18K

## Slide 11: Challenges
No current challenges
Charge: 1,2

## Slide 12: Final Design Status
All Ring Utilities Final Design Reviews are complete
No open recommendations
Charge: 6

## Slide 13: Installation Plans
P.4.5.2 Main Ring Dipole Transformer Upgrade
  Installation scheduled for October 21 (Outage FY22A)
    Pre-work: Install conduit / wiring from PP to transformers
    Outage: Install fan kits and controls
P.4.5.3 RN-03 Magnet Power Supply DI Cooling Water Upgrade
  Pre-outage construction scheduled to start in November 22
    Pump foundations and pumps
    Piping fabrication
    Cable tray & conduit installation
  Outage construction scheduled for February 23 (Outage FY23A)
    Piping demo and make the tie ins to the new pumps
    Install additional heat exchanger plates
    Install Instrumentation and wiring
  P.4.5.4 PFN Room HVAC
      PCR processed in August has shifted installation forward to March 22
Charge: 4,5

## Slide 14: Estimate to Complete
Charge: 4
We are 25% complete in Ring Utilities (Design and PM)
Procurement and installation is remaining

## Slide 15: Estimate to Complete by FY
Charge: 4
FY22 labor is Main Ring Dipole Transformer Upgrade
FY23 labor & material is PFN HVAC and RN-03 Pump Upgrades
  PFN HVAC and RN-03 are turnkey subcontracts

## Slide 16: Labor Profile
Charge: 4
Labor is largely support of turnkey installations (PFN HVAC and RN-03)
FY22 is primarily Main Ring Dipole Transformer Upgrade
FY23 is PFN HVAC & RN-03 Pump Upgrades

## Slide 17: P.4 Ring May 2021 Status Summary Schedule
Charge: 4

## Slide 18: P.04.05 Utilities Risk Register
No active risks identified
  No risks retired
High Risks
  No high risks identified
Risks are reviewed on a regular basis
Charge: 5

## Slide 19: Responses to Recommendations
No recommendations from the CD 2/3 review
Recommendations from prior DOE reviews are closed
Charge: 6

## Slide 20: ESH&Q and COVID-19 Impacts
ESH&Q impacts
  None
COVID-19 impacts
  None
Charge: 3,5

## Slide 21: 12-Month Look-Ahead
P.4.5.2 Main Ring Dipole Transformer Upgrade
  Installation scheduled for October 21 (Outage FY22A)
P.4.5.3 RN-03 Magnet Power Supply DI Cooling Water Upgrade
  Prepare SOW and Tech Spec for Water Cooling Components in April 22
  Procurement Readiness Review for Water Cooling Components in May 22
  Review and award installation contract August 22
  Installation scheduled to start November 22
  P.4.5.4 PFN Room HVAC
  Prepare SOW for PFN Room Cooling HVAC installation October 21
  PRR for PFN Room Cooling HVAC installation November 21
  Procure PFN HVAC Units as GFE in November 21
  Review and award installation contract January 22
  Install PFN HVAC Units March 22 (Outage FY22B)
Charge: 4,5

## Slide 22: Summary
P.4.5.2 Main Ring Dipole Transformer Upgrade
  Fan kits are on order with installation scheduled for October 21 (Outage FY22A)
  No foreseen issues
P.4.5.3 RN-03 Magnet Power Supply DI Cooling Water Upgrade
  Design is complete with installation contract PRR scheduled in May 22
  Installation scheduled to start in November 22
  No foreseen issues
  P.4.5.4 PFN Room HVAC
  Design is complete with HVAC procurement scheduled for November 21
  Installation scheduled for March 22
  No foreseen issues