## Slide 1: ORNL Machine Learning HVCM Use Case
Task Team
T. Britton, D. Lu, M. Radaideh, C. Pappas, P. Ramuhalli, K. Rajput, M. Schram, L. Vidyaratne, J. Walden

## Slide 2: Content
HVCM at SNS
GAN for data Augmentation
RNN autoencoders for anomaly detection
CNN autoencoders for anomaly detection
Modeling of capacitor degradation with CNN
Summary

## Slide 3: SNS RF Systems
The SNS uses 15 High Voltage Converter Modulators to power klystrons which provide the RF used to accelerate a proton beam.
There are three basic types of HVCMs
  RFQ & Drift Tube Linac
  Coupled Cavity Linac
  Super Conducting Linac
RFQ-DTL
CCL
SCL

## Slide 4: HVCM Reliability

## Slide 5: HVCMs at SNS
High Voltage Converter Modulators (HVCMs) are used to convert 13.8 kVAC, 3 φ into a train of up to 135 kV, 1.3 µs pulses at 60 Hz to klystrons which power the accelerating cavities at the SNS.
They consist of
  a) AC switch gear and magnetics
  b) a controlled rectifier to convert the input AC to 2100 VDC
  c) energy storage, chopping of the 2.1 kVDC at 20 kHz, stepping the chopped voltage up to high voltage, and rectifying the filtering the chopped high voltage.
  d) HVCM controller

## Slide 6: HVCM Schematic
HV power transformer and line filters cabinet, outside
6 pulse, phase controlled rectifier rack
Energy storage capacitors
Insulated Gate Bipolar Transistor switches, 20 kHz switching frequency
HV pulse transformers, 20 kHz bipolar pulses
Resonant Capacitors
3 phase, full wave rectifiers, 120 kHz apparent switching
Output filtering
Klystrons

## Slide 7: HVCM Waveforms
Each HVCM digitizes 32 waveform channels at 50 MS/s and saves a RUN file, decimated to 2.5 MS/s 30 minutes after start up, or after tuning has occurred.
In addition to the RUN files, two Fault files are saved every time there is a HVCM fault. One with 50 MS/s and a record length of 3.5 ms, and another at 2.5 MS/s and a record length of 36 ms, both centered at the time of the fault.
A SETTINGS file is saved whenever a change is made HVCM settings used for tuning or to set warning and fault levels.
All RUN, Fault and SETTINGS files have been archived since January 2021.

## Slide 8: Simulated HVCM Waveforms
SPICE circuit models for the HVCMs have been developed and validated.
Models have been built to also include frequency modulation using MatLab with LTSpice.
MatLab is also being used to sweep ranges of component values to generate SPICE simulations to model degradation of components such as plastic film capacitors.

## Slide 9: HVCM Faults, IGBT Exploded
Normal IGBT and flux after tuning, several days before event.
Exploded IGBT and flux from shot immediately precent event.

## Slide 10: HVCM Tuning
HVCM circuit
20 kHz nom. switching
Output voltage droop
20 kHz fixed
Droop compensation by modulating frequency from 20-23 kHz
Modulator Gain
Vs Frequency
HVCMs are tuned whenever maintenance is performed to optimize pulse flat top and keep waveforms within preset limits.
The knobs used are
  the range of frequencies to sweep during the pulse to correct for voltage droop
  shortening of the initial pulses to prevent overshoot on the rising edge
  biasing of the transformer core to prevent core saturation
  Changing the angles of the three phases and small changes in the angles of individual micro-pulses to correct for output voltage ripple.

## Slide 11: Content
HVCM at SNS
GAN for data Augmentation
RNN autoencoders for anomaly detection
CNN autoencoders for anomaly detection
Modeling of capacitor degradation with CNN
Summary

## Slide 12: From Anomaly Detection to Fault Classification
Sample size is about ~6000 samples/pulses from all 15 modulators
Normal pulse is 82.5% (removed to show better scale)
Data relabeled into 9 major classes: 1 normal, and 8 faulty.

## Slide 13: Failure detection with the help of GAN
Due to the unfair split between faulty and normal data, we use generative adversarial networks (GAN) to generate synthetic failure data that mimic real faulty data.
Then a CNN/LSTM model can be used for either binary failure classification or multi-class classification.
Performance of the CNN classifier is very good on normal data, but poor on classifying faulty data.

## Slide 14: GAN Architecture
Noise
Waveforms
Generator
Discriminator

## Slide 15: GAN on Normal Data
Epoch = 1
Epoch = 200
Epoch = 1000
Epoch = 5000
Epoch = 10000

## Slide 16: GAN on Normal Data

## Slide 17: Content
HVCM at SNS
GAN for data Augmentation
RNN autoencoders for anomaly detection
CNN autoencoders for anomaly detection
Modeling of capacitor degradation with CNN
Summary

## Slide 18: Data (from raw to processed)
1- Cut the 1.8ms pulses from the waveform
2- Get ALL normal pulses
3- Get ONLY first faulty pulse
4- Stack the pulses in a time sequence
5- Apply spectral Fourier transform for signal smoothing
6- Normalize the data between 0 and 1
Can we develop a model that detects the anomaly at the pre-fault pulse?

## Slide 19: Recurrent AutoEncoders (RAE)
Recurrent neural networks perform well in time sequences.
Autoencoders are systems used for dimensionality reduction and self-reconstruction.
The logic is: Can we train a system that learns how to accurately reconstruct itself in normal situations?
  What would happen if the system experiences an anomalous situation?
GRU: Gated Recurrent Unit
LSTM: Long Short-term memory
ConvLSTM: Convolutional LSTM

## Slide 20: Anomaly Detection Results
Area under the ROC curve (AUC)
AUC=0.5 (Random baseline detector)
AUC=1.0 (Perfect detector)
Radaideh et al. (2022). Time Series Anomaly Detection in Power Electronics Signals
with Recurrent and ConvLSTM Autoencoders. Under ORNL internal Review, to be submitted to Digital Signal Processing.

## Slide 21: Benchmarking
>
GRU: Gated Recurrent Unit
LSTM: Long Short-term memory
ConvLSTM: Convolutional LSTM
IF: Isolation forests
SVM: Support vector machine
LOF: Local outlier factor
FNN: feedforward neural network
False Omission rate
Radaideh et al. (2022). Time Series Anomaly Detection in Power Electronics Signals
with Recurrent and ConvLSTM Autoencoders. Under ORNL internal Review, to be submitted to Digital Signal Processing.

## Slide 22: Content
HVCM at SNS
GAN for data Augmentation
RNN autoencoders for anomaly detection
CNN autoencoders for anomaly detection
Modeling of capacitor degradation with CNN
Summary

## Slide 23: Goal
Detection of anomalous operation in HVCM modules
  Looking at the waveforms of HVCM modules in operation to detect anomalous pulses
  Given the pulse immediately before the faulted pulse is available, can we predict imminent failure?
Normal Data
Fault Data

## Slide 24: HVCM Anomaly Detection
Data Pre-processing
Extraction of pulses for analysis
Extract first pulse (impending fault) for analysis
Identifying anomalous ‘normal’ data
normal
Faulty normal
Box plot analysis to identify faulty normal traces
quantile statistics provide good separation
Faulty normal
normal
Threshold
Distribution of data in a module

## Slide 25: HVCM Anomaly Detection with CNN
Model
  Generalized VAE architecture for Anomaly Detection
    Applicable for data from multiple Modules
    Additional encoder-decoder branch for module ID
    1D ResNet blocks in Encoder for improved and stable representation learning

## Slide 26: HVCM Anomaly Detection
Results
  Dataset using data from 14 HVCM modules
  Training with 5-fold cross validation
  Anomaly detection by inspecting reconstruction error (MSE) of VAE

## Slide 27: HVCM Anomaly Detection
Example reconstruction results

## Slide 28: HVCM Anomaly Detection
Future Work
  Revisit pre-processing for data from modules ‘SCL5’ and ‘SCL14’
    Data from these modules contain a large variety of ‘normal’ anomalies
  Hyper-parameter tuning for VAE
    Further improvement in ROC may be obtained by hyper-parameter tuning
  Compare performance with other anomaly detection techniques
  Experiment on the possibility of leveraging the model for fault type identification

## Slide 29: Content
HVCM at SNS
GAN for data Augmentation
RNN autoencoders for anomaly detection
CNN autoencoders for anomaly detection
Modeling of capacitor degradation with CNN
Summary

## Slide 30: Goal
Ultimately, we want to predict when components will need (preventative) maintenance
  Can we look at the waveforms of an HVCM in operation and predict the capacitances of the three phases?
  Not a lot of data-measurement correlation. So, we'll start with simulations

## Slide 31: method
We utilized high fidelity simulations (LTspice) of the HVCM
  Simulate the 10 traces present in data
    VOUT
    IAP
    IAPS
    IBP
    IBPS
    ICP
    ICPS
    Aflux
    Bflux
    Cflux
Index-600 (the "stable" region)
IAP
Current traces contain artifacts from LTspice convergence. They are cleaned before training

## Slide 32: model
Basic premise:
  Extract/synthesize features
    Each Conv1D block also contains Batch normalization, average pooling, and dropout
  Use those features to compute the 3 capacitance values
    Each MLP block contains 6 nodes connected to an output
    There are no connections between MLP blocks, thus no correlated computation of values
Conv1D
Conv1D
Conv1D
Conv1D
Flatten
MLP
MLP
MLP
CA
CB
CC

## Slide 33: Results
Training performed with 5-fold cross validation
  676 samples withheld from training as a test set
  Mean absolute percentage error for loss
Run File | CA | CB | CC
CCL1_400ns_Run_8.31.2021-2.54.19PM | 3135.7764 pF | 3369.5867 pF | 3419.5261 pF

## Slide 34: Future work
Hyper parameter optimization
Uncertainty quantification
  Multi methods
Model validation
  Check prediction on real data temporally proximate to when the capacitors are measured
Use these methods to make predictions
  RNN?

## Slide 35: Content
HVCM at SNS
GAN for data Augmentation
RNN autoencoders for anomaly detection
CNN autoencoders for anomaly detection
Modeling of capacitor degradation with CNN
Summary

## Slide 36: Goals of Machine Learning for the HVCM Use Case
The overall goal for machine learning for the HVCM case is improved reliability and the reduction of unscheduled down time of the HVCMs through anomaly detection methods (In a good progress).
Predict degradation of components such as plastic film capacitors which happens slowly with time and schedule HVCM maintenance to prevent catastrophic faults and loss of beam time for SNS (In a good progress).
Automate HVCM tuning to keep it optimal as conditions change such as when components degrade or with temperature variations (Not moving well, Issues with data streaming).

## Slide 37: Work in Progress
Testing GAN to generate faulty data. This includes data augmentation by adding noise to current fault data, and generate some fault events from simulation.
Collecting more data from the RFTF test bed.
Capacitor degradation work to be finalized/improved by adding uncertainty bands.
Getting some papers done on anomaly detection, capacitor degradation, ML for HVCM.