## Slide 1: OACTree
Using behavior trees to automate operations and control
(or “How to plant an OACTree”?)
Robert Gunion, Gennady Pospelov, Walter Van Herck

## Slide 2
A MULTINATIONAL SCIENCE AND R&D COLLABORATION
Mission: to demonstrate key aspects of fusion’s scientific and technological feasibility.
Integrated operation of technologies for a fusion power plant
Production and control of a self-heating “burning plasma”
Safety demonstration

## Slide 3: Goals & requirements
ITER's operation requires complex automation sequences that are beyond the scope of the finite state machine concept that the EPICS SNL Compiler/Sequencer implements (PvAccess?).
ITER needs a framework for monitoring, configuration & coordinated control of plant system I&Cs with the following requirements:
Create/execute operational procedures in a robust, repeatable and traceable way
Support concurrency/reactivity
Extensible
Composable
Maintainable
Required quality assurance level

## Slide 4: Goals & requirements
Start pumps for cooling water loop
* Initialization: select pumps to use
* Check electrical systems
* Check switchgear
* Check interlocks
* Pressurizer pressure control
* Check pressure controller
* Set pressure setpoint
* Pressurizer level control
* Check demineralized water distribution
* Check level controller
* Set level setpoint
...

## Slide 5: Behavior trees

## Slide 6: Strengths
Handling of complexity
  Split tasks into sequences or alternative solutions
  Compose larger trees out of smaller ones: scalability
  Goal-oriented semantics
Reactivity
Modular nature and maintainability
  Easy to replace nodes
  Simple interface allows simple extension
Locality: small changes lead to small changes in outcome

## Slide 7: What is OACTree?
A C++ framework for creating and executing operational procedures using behavior trees:
Definition of instruction node and variable API
Common instructions for control flow (sequence, fallback, repeat, parallel, etc.)
Very basic variable implementations (in memory, file)
User I/O API
Plugin system
Concurrency
Command line applications to validate/execute procedures
GUI to create/edit/execute procedures
Plugins for ITER control system (EPICS, MathExpr, etc.)

## Slide 8: Example

## Slide 9: Plugins

## Slide 10: Plugins
Control: common control logic; e.g. WaitForCondition
Mathexpr: evaluate mathematical expressions
EPICS plugin:
  ChannelAccess: read/write PV instructions; client variable
  PvAccess: read/write PV instructions; client and server variables; RPC client instruction
ITER specific: plant system configuration and pulse schedule handling

## Slide 11: PvAccess counter

## Slide 12: PvAccess monitor

## Slide 14: OACTREE at ITER
Demineralized water plant operational efficiency assessment
Start/stop/monitor cooling water loops
Translation of plant system states into common operational states
Snapshot/restore of plant system configurations

## Slide 15: CC2D startup

## Slide 16: Roadmap
Improve GUI
  functionality (e.g. undo/redo)
  user experience
Automation servers and clients
  Enable dedicated servers to run operational procedures
  Enable multiple clients to monitor/control the execution of those procedures
Collaboration & outreach
  Facilitate building/packaging on non-ITER systems
  Make source available on public website
  Collaborations