## Slide 1: Transitioning to EPICS at EIC: UDP-Based Waveform Monitoring
EPICS Collaboration Meeting
September 17, 2024
Kyle A. Fahey
Electrical Engineer

## Slide 2: Outline
Pre-Existing Interfaces
  EPICS Interface
  UDP Interface
Workflow for Waveform Conversion
  Python
  EPICS-ADO Bridge
  LogView
Conclusion
2024 EPICS Collaboration Meeting
Kyle A. Fahey

## Slide 3: EPICS Interface for Arc Detector
2024 EPICS Collaboration Meeting
Kyle A. Fahey
Modified CS-Studio UI
BNL’s Pet view
Arc detector chassis provided by Jefferson Lab for performance evaluation
  IOC for controls and statuses provided
  EDM UI provided, converted to CS-Studio by Latif Kabir
EPICS PVs usable in BNL systems
  ADO exists to mirror PV data
  Pet pages
  Logged data
EPICS PVs can be used to set up arc test conditions with onboard LED

## Slide 4: UDP Interface for Arc Detector
UDP Interface provides more functionality
  Controls to simulate an arc condition
  Ability to view raw waveform data
  Ability to quickly reset all parameters
Communicates via Python script given by JLAB
  Waveform viewable through matplotlib
Data is not readily available for use in BNL systems
  We want to periodically save raw waveform data
2024 EPICS Collaboration Meeting
Kyle A. Fahey
Normal Waveform
Arc Test Waveform

## Slide 5: Waveform Workflow
2024 EPICS Collaboration Meeting
Kyle A. Fahey
Arc Detector
EPICS IOC
ADO Device
Logged Data
Python Script
EPICS-ADO Bridge
LogView

## Slide 6: Python Script
Uses caproto library
  Implementation of Channel Access protocol in Python, found at https://caproto.github.io/
Periodically runs through all ADCs to get raw waveform data
Hooks into separate “softIoc” process
  Getting data from waveforms takes too long for an internal IOC to handle requests
2024 EPICS Collaboration Meeting
Kyle A. Fahey
Calling waveform function for all waveforms periodically
Waveforms for the 3 connected detector heads

## Slide 7: EPICS-ADO Bridge
Designed at BNL
  Interface Between EPICS and ADO – (Andrei Sukhanov, James Jamilkowski)
Translates EPICS PVs for use with ADO software
  Pet
  LogView
Simple Setup
  Create mapping file
  Create ADO definition in manager application
  Run bridge, pointing to mapping file
2024 EPICS Collaboration Meeting
Kyle A. Fahey
Definition of EPICS-ADO Bridge Parameters
Pet Page for ADO Generated by EPICS-ADO Bridge

## Slide 8: LogView
Application written by BNL to save ADO data over time
Logreq file defines ADOs to point to
Set up using General Purpose Monitor application
2024 EPICS Collaboration Meeting
Kyle A. Fahey
Logged Normal Waveform
Logged Arc Test Waveform

## Slide 9: LogView Over Time
Allows for long-term monitoring of values
2024 EPICS Collaboration Meeting
Kyle A. Fahey
Logged Waveforms of 3 Connected Detector Heads
Logged Waveforms of Detector Head #2 Over Several Days

## Slide 10: Conclusion
EIC LLRF is testing an arc detector chassis from Jefferson Lab, which includes EPICS functionality
Raw waveform data was not included in the provided IOC, but accessible over UDP commands
Python script was created to periodically request waveform data and integrate it into an EPICS IOC
EPICS IOC converted for use with BNL’s LogView software using EPICS-ADO Bridge
Arc detector is being monitored reliably since July 2024
2024 EPICS Collaboration Meeting
Kyle A. Fahey

## Slide 11
2024 EPICS Collaboration Meeting
Kyle A. Fahey