## Baseline January 2017 Working
RAD Global Priorities
[12 empty] | Criterion 1 | Criterion 2 | Criterion 3 | Criterion 4 | Criterion 5 | Criteria Scores |  |  | Probability | Consequence | Risk | Safety | Overall Impact | Notes
Criterion: | [11 empty] | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects |  |  |  | Estimated Frequency of Downtime Event if Project not Undertaken | Estimated Duration of Downtime Event if Project Not Undertaken | Product of Probability and Consequence | Personnel Safety
Criterion Scope: | [11 empty] | • >5000 hours of scheduled neutron production • 100% predictability • ≥90% reliability against schedule • minimize down times ≥3 hours | • operate at 1.4 MW • provide additional margin for 1.4 MW operation • support progress toward 2 MW operation for FTS | • enhance the capability of more than one neutron scattering instrument • enhance the capability of the neutron source to support all instruments • advance accelerator science or technology with possible application the neutron source | • Technical action item from an external review (e.g. NAB, DOE, AAC, ASRC) • Technical action item from an internal review or assessment • Technical action item from an operational event or a regulatory requirement • PEMP or other primary sponsor commitment | • Project is on approved current year science priority list but not time critical, LDRD or externally funded limited term • Project is on approved science priority list with specific actions to address • Project is on science priority list for out year consideration • Project is not on science priority list or not considered |  |  |  | • Once a week • Once a month • Once a quarter • Once a year • Once every 2 years or longer | • One year or more • 3 months to one year • 1 to 3 months • 1 week to 1 month • 1 day to 1 week |  | Risk of injury of varying severity or of fatality to workers
Scoring Rules for each Criterion: | [11 empty] | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If not on list score 0; if out year consideration score 3; if planning stage score 6; if current year execution score 9 |  |  |  | If once a week, score 5; if once a month score 4; if once a quarter score 3; if once a year score 2; if once every 2 years or longer, or no likely downtime score 1. | If one year or more score 5; if 3 months to 1 year score 4; if 1 to 3 months score 3; if 1 week to 1 month score 2; if 1 day to 1 week score 1 |  | If No Risk of Injury to Personnel score a 1; if possible recordable injury score 10; if possible DART case score 50; if possible fatality score 100
Guidance: | [11 empty] | Evaluate whether the project directly affects the ability of the facility to meet the four scope elements listed above and score accordingly. | Evaluate whether the project will affect operating power capability according to the criteria and score accordingly. | Evaluate the project to determine whether it enhances capability of more than one instrument, or the accelerator, or is a funded external project and score accordingly. | Determine whether the project must be done in response to one or more external drivers, and score accordingly. | Determine the status of the project on the current approved instrument upgrade plan and score accordingly. |  |  |  | Perform a qualitative assessment of the frequency of system-related downtime events if the project is not performed. | Perform a qualitative assessment of the duration of the downtime for each occurrence if the project is not performed |  | Perform a qualitative assessment of the impact that not undertaking the activity will have on personnel safety
Weighting Factor: | [11 empty] | 4 | 3 | 2 | 2 | 8 |  |  |  | 1 | 1 |  | 10
Project Identifier | Management Status | Project | Commitment (PEMP or Business Plan) | Owning Division | Owning Group | Project Lead | Project Type | Status | Non-Outage Schedule | Outage Schedule | Category | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects | Weighted Score (Criteria 1-4) | Science Score (Criterion 5) | Total Score (Criteria 1-5) | Probability (1-5) | Consequence (1-5) | Risk (1-25) | Risk of Injury to Personnel | Overall Impact | Notes
EERF-20 | Approved | LEBT smart chopping | Yes | RAD | EERF | Champion | OIP | Active | Now to 2017B |  | Low Cost Improvement | 6 | 6 | 6 | 0 | 0 | 54 | 0 | 54 | 1 | 1 | 1 | 0 | 5.4 | FY2017 Business Plan Objective 2.c.2.
SCLS-10 | Approved | CM9, CM19 insulating vacuum backflow preventer improv. | No | RAD | SCLS | Kim | OIP | Active | Now to 2017B | 2017B (May-June) | Low Cost Improvement | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 2 | 3 | 6 | 0 | 27 | Some Controls work remaining
MSO-14 | Approved | AIP-35 Warm Linac Vacuum Upgrade | Yes | RAD | MSO | Stone | AIP | Active | Now to 2017B | 2017B (May-June) | Obsolescence | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 5 | 1 | 5 | 0 | 21 | FY2017 Business Plan Objective 3.c.
EERF-01B | Approved | AIP-34 HVCM Controller Upgrade | Yes | RAD | EERF | Champion | AIP | Active | Now to 2017B | 2017B (May-June) | Obsolescence | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 3 | 1 | 3 | 0 | 19.8 | FY2017 Business Plan Objectives 2.c.2 and 3.c.
CON-08 | Approved | Isolate FE PPS Cabinets | No | RAD | CON | Mahoney | OIP | Active | Now to 2017B | 2017B (May-June) | Efficiency | 9 | 3 | 0 | 9 | 0 | 63 | 0 | 63 | 1 | 3 | 3 | 0 | 18.9
CON-03 | Approved | Install high power shutters DTL1/2 waveguide | No | RAD | CON | White | OIP | Active | Now to 2017B | 2017B (May-June) | Efficiency | 9 | 3 | 3 | 3 | 0 | 57 | 0 | 57 | 3 | 1 | 3 | 0 | 17.1
SCLS-05A | Approved | Plasma processing in the tunnel | Yes | RAD | SCLS | Kim | OIP | Active | Now to 2017B | 2017B (May-June) | Low Cost Improvement | 3 | 9 | 3 | 6 | 3 | 57 | 24 | 81 | 1 | 1 | 1 | 0 | 8.1 | FY2017 Business Plan Objective 2.c.2. Goal is two cryomodules will be processed in summer 2017. 3-4 additional cryomodules will be processed during the maintenance for IRP change
CON-10 | Approved | Timing Master Installation | No | RAD | CON | Curry | OIP | Active | Now to 2017B | 2017B (May-June) | Obsolescence | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 1 | 2 | 2 | 0 | 7.2
EERF-33 | Approved | Install new circulator on DTL2 RF station | No | NScD | EERF | Moss | OIP | Active |  | 2017B (May-June) | Spare | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 1 | 2 | 0 | 7.2 | Continuation of campaign to replace or rebuild all RFQ and DTL circulators.
MSO-07 | Authorized | Helium Gas Injection | Yes | ISD | SDEA | Jacobs | OIP | Active | Now to 2017C | 2017C (October) | Low Cost Improvement | 9 | 9 | 3 | 6 | 0 | 81 | 0 | 81 | 3 | 2 | 6 | 10 | 58.6 | FY2017 Business Plan Objective 2.c.2.
MSO-04 | Authorized | IRP Replacement | Yes | RAD | MSO | Baumgartner | OIP | Active | Now to 2018A | 2018A (December-April) | Efficiency | 9 | 0 | 6 | 3 | 0 | 54 | 0 | 54 | 2 | 5 | 10 | 0 | 54 | FY2017 Business Plan Objective 2.d.4.
EERF-12 | Authorized | Installation of new RFQ at Front-End building | Yes | RAD | EERF | Champion | OIP | Active | Now to 2018A | 2018A (December-April) | Low Cost Improvement | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 2 | 4 | 8 | 0 | 52.8 | FY2017 Business Plan Objective 2.c.2.
MSO-17 | Authorized | LINAC Plug Door Replacement | No | RAD | MSO | Roseberry | OIP | Active | Now to 2018A | 2018A (December-April) | Safety | 0 | 0 | 0 | 3 | 0 | 6 | 0 | 6 | 1 | 1 | 1 | 50 | 50.6 | Safety issue
MSO-37 | Authorized | SNS RFQ Inlet Flange Upgrade | No | RAD | E&RF | Roseberry | OIP | Active | Now to 2018A | 2018A (December-April) | Low Cost Improvement | 9 | 9 | 3 | 3 | 0 | 75 | 0 | 75 | 1 | 5 | 5 | 0 | 37.5 | The SNS RFQ inlet flange needs improvement for performance and maintainability of the LEBT chopper target
MSO-38 | Authorized | RFQ Transportation | No | RAD | MSO | Roseberry | OIP | Active | Now to 2018A | 2018A (December-April) | Safety | 9 | 9 | 3 | 3 | 0 | 75 | 0 | 75 | 2 | 2 | 4 | 0 | 30 | Transporation Fixtures and Dolly are needed to safely move the new RFQ from 8320 ot 8100
SCLS-05B | Approved | Plasma processing in the tunnel | Yes | RAD | SCLS | Kim | OIP | Active | Now to 2018A | 2018A (December-April) | Low Cost Improvement | 3 | 9 | 3 | 6 | 3 | 57 | 24 | 81 | 1 | 1 | 1 | 0 | 8.1 | FY2017 Business Plan Objective 2.c.2. Goal is two cryomodules will be processed in summer 2017. 3-4 additional cryomodules will be processed during the maintenance for IRP change
MSO-05 | Authorized | HWS #4 Heavy Water Conversion | Yes | RAD | MSO | Jacobs | OIP | Active | Now to 2018A | 2018A (December-April) | Low Cost Improvement | 0 | 0 | 6 | 3 | 3 | 18 | 24 | 42 | 1 | 1 | 1 | 0 | 4.2 | FY2017 Business Plan Objective 2.d.4.
SCLS-01 | Authorized | Medium Beta Spare Cryomodule | No | RAD | SCLS | Kim | OIP | Active | Level of Effort | Unscheduled | Spare | 9 | 9 | 0 | 3 | 0 | 69 | 0 | 69 | 2 | 2 | 4 | 0 | 27.6
MSO-15 | Authorized | AIP-36 HVCM Cooling Upgrade | Yes | RAD | MSO | Schubert | AIP | Active | Unscheduled | Unscheduled | Low Cost Improvement | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 3 | 1 | 3 | 0 | 18.9 | FY2017 Business Plan Objective 3.c.
CON-01 | Authorized | AIP-39 Machine Protection System Improvements | Yes | RAD | CON | White | AIP | Active | Now to 2018C | Unscheduled | Obsolescence | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 3 | 3 | 9 | 0 | 56.7 | FY2017 Business Plan Objective 3.c. In design, implementation will require AIP fuding, schedule changed to Level of Effort
IDAC-05 | Approved | CNCS DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Active | Now to 2017B | 2017B (May-June) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6
IDAC-06 | Approved | EQ-SANS DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Active | Now to 2017B | 2017B (May-June) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6
IDAC-07 | Approved | Vulcan DAQ Upgrade | No | RAD | IDAC | Hartman | OIP | Active | Now to 2017B | 2017B (May-June) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6
IDAC-04 | Approved | ARCS DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Active | Now to 2018A | 2018A (December-April) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6 | Linked to INS-17, ARCS Detector Modernization.
IDAC-08 | Approved | MagRef DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Active | Now to 2018A | 2018A (December-April) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6
IDAC-09 | Approved | SNAP DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Active | Now to 2018A | 2018A (December-April) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6
IDAC-10 | Approved | WAND DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Active | Now to 2018A | 2018A (December-April) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6
INS-05 | Approved | POWGEN Phase I Upgrade | Yes | CEMD | CHEMCRYS | Huq | Instrument Upgrade | Active | Now to 2017B |  | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-01A | Approved | NOMAD background reduction Phase 1 | Yes | CEMD | ADVDIFF | Tucker | Instrument Upgrade | Active | Now to 2017B | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-03 | Approved | Magnetism Reflectometer Improvement Project | Yes | QCMD | TFN | Fitzsimmons | Instrument Upgrade | Active | Now to 2017B | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-04A | Approved | EQ-SANS Detector Vessel/Sample Area Modifications Phase 1 | Yes | BSMD | SDSM | Heller | Instrument Upgrade | Active | Now to 2017B | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-10A | Authorized | SNAP detector rebuild Phase 1 | Yes | ISD | ADVDIFF | Tulk | Instrument Upgrade | Active | Now to 2017B | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 2 | 1 | 2 | 0 | 14.4 | FY 2017 Business Plan Objective 2.d.3.
INS-13 | Approved | CORELLI Thimble | Yes | ISD | SOM | Ye | Instrument Upgrade | Active | Now to 2017B | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-01B | Approved | NOMAD background reduction Phase 2 | Yes | CEMD | ADVDIFF | Tucker | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-04B | Approved | EQ-SANS Detector Vessel/Sample Area Modifications Phase 2 | Yes | BSMD | SDSM | Heller | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-06 | Approved | TOPAZ Goniometer | Yes | CEMD | CHEMCRYS | Huq | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-07 | Approved | SEQUOIA Vacuum Upgrade | Yes | ISD | MSO | Jones (L) | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY2017 Business Plan Objective 2.d.3. Duplicate with MSO-11 so retained this and eliminated MSO-11. Price/Stone are points of contact within MSO for this project.
MSO-10 | Approved | BL17 Turbo Integration--SCHW Cooling | No | RAD | MSO | Jacobs | OIP | Active | Now to 2018A | 2018A (December-April) | Low Cost Improvement | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY2017 Business Plan Objective 2.d.3. Linked to INS-07.
INS-09 | Authorized | 14T Magnet for SNS | Yes | ISD | SE | Stone | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Capability | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY2017 Business Plan Objective 2.d.3.
INS-10B | Authorized | SNAP detector rebuild Phase 2 | Yes | ISD | ADVDIFF | Tulk | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 2 | 1 | 2 | 0 | 14.4 | FY 2017 Business Plan Objective 2.d.3.
INS-14 | Authorized | CNCS collimator | Yes | ISD | TOF | Ehlers | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-17 | Authorized | ARCS Detector Modernization | No | ISD | TOF | Abernathy | Instrument Upgrade | Active | Now to 2018A | 2018A (December-April) | Obsolescence | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 3 | 1 | 3 | 0 | 21.6 | FY 2017 Business Plan Objective 2.d.3. Linked to IDAC-04, ARCS DAQ/Controls Upgrade.
INS-18 | Authorized | POWGEN T0 Chopper Baseplate | No | ISD | CHEMCRYS | Stockton | OIP | Active | Now to 2018A | 2018A (December-April) | Obsolescence | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 3 | 3 | 0 | 21.6
PPU-01 | Authorized | Proton Power Upgrade | Yes | PPU | PPU | Galambos | Facility Upgrade | Active | Level of Effort | Unscheduled | Facility Upgrade | 0 | 9 | 9 | 9 | 9 | 63 | 72 | 135 | 1 | 1 | 1 | 0 | 13.5 | FY2017 Business Plan Objective 2.e.a. Need mechanical and electrical support
APBIIS-02 | Authorized | 6D phase space grant | Yes | RAD | APBIIS | Cousineau | MIE | Active | Beam Test Facility |  | Research and Development | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY2017 Business Plan Objective 3.c. Need mechanical and electrical support
SSG-06 | Authorized | Tie-in and Valving for Second Elevated Water Storage Tank | No | DOO | SITE | McLaughlin | Facility Upgrade | Pending Planning | Now to 2017B | 2017B (May-June) | Capability | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 1 | 1 | 1 | 0 | 8.4 | Summer outage provides an opportunity to execute this work with minimal impact on operations.
EERF-32 | Authorized | Installation of old RFQ at BTF | Yes | RAD | EERF | Champion | OIP | Active | Beam Test Facility | Unscheduled | Low Cost Improvement | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 2 | 4 | 8 | 0 | 52.8 | FY2017 Business Plan Objective 2.c.2.
MSO-30 | Approved | Replace Obsolete MKS Gauge Controllers | No | RAD | MSO | Price | OIP | Active |  | 2017B (May-June) | Obsolescence | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 3 | 1 | 3 | 0 | 7.2
MSO-40 | Approved | Target Vacuum - PBW Interstitial Upgrade | No | RAD | MSO | Price | OIP | Active |  | 2017B (May-June) | Obsolescence | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 3 | 1 | 3 | 0 | 3.6 | Current pumping sytem is completely obsolete
EERF-28 | Approved | CCL RF Window Temperature Measurement | No | RAD | EERF | Champion | OIP | Active |  | 2017B (May-June) | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 1 | 1 | 1 | 0 | 1.2
MSO-31 | Approved | Replace RTBT T-SectionTurbos / Controllers | No | RAD | MSO | Price | OIP | Pending Resources |  | 2017B (May-June) | Low Cost Improvement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0
MSO-36 | Authorized | Gamma Blocker Switch Upgrade | No | RAD | MSO | Roseberry | OIP | Pending Funding |  | 2018A (December-April) | Safety | 0 | 0 | 0 | 6 | 0 | 12 | 0 | 12 | 2 | 1 | 2 | 10 | 12.4 | A switch lever in the RID Gamma blocker has bent previously - preventing PPS re-certifcation after an outage. A new design for a more robust, rapidly replaceable switch module should be developed
MSO-39 | Authorized | Target Vacuum - Target Interstitial Vacuum Upgrade | No | RAD | MSO | Price | OIP | Active |  | 2018A (December-April) | Obsolescence | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 3 | 1 | 3 | 0 | 3.6 | Current pumping sytem is completely obsolete
INS-02 | Authorized | NOMAD sample changer | Yes | ISD | SNSINST | Everett | Instrument Upgrade | Active | Now to 2018B | 2018B (July-August) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-08 | Approved | NSE Magnetism Capability | Yes | ISD | TOF | Ehlers | Instrument Upgrade | Active | Now to 2019B | 2019B (July-August) | Capability | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-15 | Authorized | HYSPEC elevator | Yes | ISD | TOF | Winn | Instrument Upgrade | Active | Now to 2018B | 2018B (July-August) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
EERF-09 | Approved | Procure spare DTL circulators | No | RAD | EERF | Champion | OIP | Active | Long Lead Procurements | Unscheduled | Spare | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 5 | 10 | 0 | 36 | Install third article during 2017B.
EERF-14 | Authorized | Develop alternative RF-Vacuum window source for DTL and CCL | No | RAD | EERF | Champion | OIP | Active | Long Lead Procurements | Unscheduled | Spare | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 2 | 4 | 8 | 0 | 33.6 | Continuation of work with Mega Inc.
EERF-17 | Authorized | HVCM IGBT replacement | No | RAD | EERF | Champion | OIP | Active |  | Unscheduled | Obsolescence | 9 | 6 | 3 | 0 | 0 | 60 | 0 | 60 | 4 | 1 | 4 | 0 | 24
EERF-10 | Authorized | Procure spare klystrons | No | RAD | EERF | Champion | OIP | Pending Funding | Long Lead Procurements | Unscheduled | Spare | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 5 | 5 | 0 | 22.5
EERF-11 | Authorized | Develop alternative supply chain for 2.5 and 5.0 MW klystrons | No | RAD | EERF | Champion | OIP | Pending Funding | Long Lead Procurements | Unscheduled | Supply Chain | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 5 | 5 | 0 | 22.5
APBIIS-11 | Authorized | RTBT harp electronics | No | RAD | APBIIS | Aleksandrov | OIP | Pending Planning |  | Unscheduled | Obsolescence | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 2 | 4 | 8 | 0 | 21.6 | Upgrade and spare for existing electronics
SCLS-06 | Not Authorized | SCLS vacuum improvement | No | RAD | SCLS | Kim | AIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 9 | 3 | 0 | 3 | 0 | 51 | 0 | 51 | 4 | 1 | 4 | 0 | 20.4 | Add isolation valve and small turbo pump at the cryomodule pump-drop. Install roughing pump line for the turbos. Improve insulating vacuum system.
SCLS-03 | Authorized | Spare Carbon Bed | No | RAD | SCLS | Kim | OIP | Active |  | Unscheduled | Spare | 9 | 0 | 0 | 6 | 0 | 48 | 0 | 48 | 1 | 4 | 4 | 0 | 19.2 | Bids covering the installation received 7/15/16 and are being evaluated. Requires SCLS-08
MSO-01 | Authorized | Primary Foil Changer Spare & Test Stand | No | RAD | MSO | Roseberry | OIP | Active | Level of Effort | Unscheduled | Spare | 6 | 9 | 0 | 0 | 0 | 51 | 0 | 51 | 3 | 1 | 3 | 0 | 15.3
STS-01 | Authorized | Second Target Station | Yes | STS | STS | Galambos | Facility Upgrade | Active |  | Unscheduled | Facility Upgrade | 0 | 9 | 9 | 9 | 9 | 63 | 72 | 135 | 1 | 1 | 1 | 0 | 13.5 | FY2017 Business Plan Objective 2.e.a. Need mechanical and electrical support
MSO-19 | Authorized | Chicane 02 Vacuum Vessel Upgrade | No | RAD | MSO | Roseberry | OIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 1 | 4 | 4 | 0 | 13.2 | Incorporates prior duplicate tasks APBIIS-03 (Moved to Completed Projects) and MSO-02 (Eliminated). Roseberry has lead to coordinate with Plum.
MSO-13 | Authorized | Servo-Manipulator Replacement | No | RAD | MSO | Denison | AIP | Pending Funding |  | Unscheduled | Obsolescence | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 1 | 1 | 1 | 10 | 13
MSO-28 | Not Authorized | Replace All Shutter Lifting Rods | No | RAD | MSO | Denison | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 3 | 0 | 3 | 6 | 0 | 30 | 0 | 30 | 1 | 1 | 1 | 10 | 13
MSO-12 | Authorized | RF Window "Post-Conditioned" Vacuum System | No | RAD | MSO | Price | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 2 | 2 | 4 | 0 | 12
SCLS-07 | Authorized | Engineering and hardware development for CHL 2K cold box repair | No | RAD | SCLS | Kim | AIP | Pending Planning |  | Unscheduled | Supply Chain | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 1 | 4 | 4 | 0 | 12
MSO-42 | Authorized | RFTF DIW & Glycol Instrumentation Upgrade | No | RAD | MSO | Smith, C. Craig | OIP | Design | Level of Effort | Unscheduled | Low Cost Improvement | 3 | 3 | 6 | 3 | 0 | 39 | 0 | 39 | 1 | 3 | 3 | 0 | 11.7 | RFTF DI systems are crudely instrumented. Project objective is to upgrade instrumentation and associated monitoring to provide more reliable service to Test Stand and BTF operations.
EERF-22 | Authorized | Replace RNSS-2 switch with a remotely operated switch | No | RAD | EERF | Champion | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 1 | 1 | 1 | 10 | 11.2
EERF-16 | Authorized | Develop alternative source of HVCM boost capacitors | No | RAD | EERF | Champion | OIP | Active | Long Lead Procurements | Unscheduled | Supply Chain | 6 | 6 | 3 | 3 | 0 | 54 | 0 | 54 | 2 | 1 | 2 | 0 | 10.8
MSO-24 | Authorized | Separate Front End DI Water Loop from KL-04 DI Water Systems | No | RAD | MSO | Norman | OIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 6 | 9 | 0 | 0 | 0 | 51 | 0 | 51 | 2 | 1 | 2 | 0 | 10.2
MSO-25 | Authorized | Remote auto fill of Collimators cooling skids | No | RAD | MSO | Smith, C. Craig | OIP | On Hold |  | Unscheduled | Low Cost Improvement | 6 | 9 | 0 | 0 | 0 | 51 | 0 | 51 | 2 | 1 | 2 | 0 | 10.2
EERF-19 | Authorized | PSI upgrade | No | RAD | EERF | Champion | OIP | Pending Planning |  | Unscheduled | Obsolescence | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 3 | 1 | 3 | 0 | 9.9
MSO-35 | Authorized | Cooling tower piping laterals and isolation valve replacement. | No | RAD | MSO | Smith, C. Craig | OIP | Design |  | Unscheduled | Low Cost Improvement | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 1 | 3 | 3 | 0 | 9.9 | Cooling tower later isolation valves have been abandoned in place since commissioning in 2013. Piping is standard wall carbon steel vs. more robust material. HFIR upgaded their laterals in 2016.
APBIIS-06 | Authorized | AIP-37 Beam Instrumentation Infrastructure Improvements | No | RAD | APBIIS | Aleksandrov | OIP | Pending Funding | Now to 2018C | Unscheduled | Obsolescence | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 4 | 8 | 0 | 9.6 | Linac BPM upgrade, Ring BPM upgrade, BLM upgrade
SCLS-08 | Authorized | Engineering and hardware development to keep SCL cold at around 80 K during long CHL shutdown | No | RAD | SCLS | Kim | AIP | On Hold |  | Unscheduled | Efficiency | 3 | 0 | 0 | 3 | 0 | 18 | 0 | 18 | 1 | 5 | 5 | 0 | 9 | Engineering analysis is ongoing for a cheaper solution
EERF-27 | Authorized | Install UPS for Front-End vacuum controls | No | RAD | EERF | Champion | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 9 | 0 | 0 | 3 | 0 | 42 | 0 | 42 | 2 | 1 | 2 | 0 | 8.4
MSO-26 | Authorized | Accelerator System CAD Model | No | RAD | MSO | Roseberry | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 4 | 4 | 0 | 8.4
APBIIS-12 | Authorized | Injection foil video improvement | No | RAD | APBIIS | Aleksandrov | OIP | Active |  | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 3 | 1 | 3 | 0 | 8.1 | Need mechanical designer support
EERF-18 | Not Authorized | AIP-46 Linac Quad power supply standardization | No | RAD | EERF | Champion | AIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 1 | 2 | 0 | 7.2
INS-12 | Authorized | VULCAN detector build-out | Yes | ISD | ENGMAT | An | Instrument Upgrade | Pending Planning |  | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-16 | Authorized | POWGEN: phase II detectors | Yes | ISD | CHEMCRYS | Huq | Instrument Upgrade | Pending Planning |  | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
MSO-34 | Approved | NexGen Ion Pump Controller Evaluation | No | RAD | MSO | Price | OIP | Pending Resources |  | Unscheduled | Supply Chain | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 3 | 1 | 3 | 0 | 7.2
SSG-01 | Not Authorized | RAD Shop & Assembly Building | No | NScD | SITE | McLaughlin | GPP | Pending Funding |  | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | Conceptual effort needed to establish site and funding needs
CON-07 | Authorized | Replacement for PSC | No | RAD | CON | Curry | OIP | Pending Resources |  | Unscheduled | Obsolescence | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 2 | 1 | 2 | 0 | 6.6
SCLS-09 | Authorized | VFD test stand for cold compressor | No | RAD | SCLS | Kim | OIP | Pending Planning |  | Unscheduled | Efficiency | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 2 | 1 | 2 | 0 | 6.6
CON-09 | Not Authorized | VENUS PPS Installation | No | RAD | CON | Mahoney | MIE | Pending Funding |  | Unscheduled | Efficiency | 0 | 0 | 3 | 3 | 6 | 12 | 48 | 60 | 1 | 1 | 1 | 0 | 6
EERF-02 | Authorized | HVCM Alternate Topology Modulator development | No | RAD | EERF | Champion | OIP | Active | Modulator Test Facilities | Unscheduled | Low Cost Improvement | 6 | 6 | 6 | 0 | 0 | 54 | 0 | 54 | 1 | 1 | 1 | 0 | 5.4 | Baseline design for PPU new modulators.
EERF-21 | Authorized | Procure spare substation transformers | No | RAD | EERF | Champion | OIP | Pending Funding | Long Lead Procurements | Unscheduled | Spare | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 2 | 1 | 2 | 0 | 4.8
MSO-22 | Authorized | DTL Spares Initiative | No | RAD | MSO | Roseberry | OIP | Pending Funding |  | Unscheduled | Spare | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 1 | 4 | 4 | 0 | 4.8
CON-04 | Authorized | ReplacePLCs/Panelview for Target | No | RAD | CON | Strong | OIP | Pending Resources |  | Unscheduled | Obsolescence | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 1 | 1 | 0 | 4.5 | This is really maintenance therefore I propose we remove it from this list.
EERF-04 | Authorized | Develop thryatron replacement for extraction kicker PFNs | No | RAD | EERF | Champion | OIP | Active |  | Unscheduled | Low Cost Improvement | 3 | 6 | 6 | 0 | 0 | 42 | 0 | 42 | 1 | 1 | 1 | 0 | 4.2
EERF-07 | Authorized | Development of new LLRF system | No | RAD | EERF | Champion | OIP | Active |  | Unscheduled | Low Cost Improvement | 3 | 6 | 3 | 0 | 0 | 36 | 0 | 36 | 1 | 1 | 1 | 0 | 3.6 | Essential for PPU.
SSG-02 | Authorized | Klystron Gallery HVAC System Improvements | No | RAD | SITE | McLaughlin | OIP | Pending Funding |  | Unscheduled | Efficiency | 3 | 0 | 0 | 3 | 0 | 18 | 0 | 18 | 2 | 1 | 2 | 0 | 3.6 | On-going issue with air circulation for cooling the instrument racks. Needs support from CUB (chilled water) and Controls Group.
EERF-05 | Authorized | Comprehensive update of the HVCM design drawings including red line capture | No | RAD | EERF | Champion | OIP | Active |  | Unscheduled | Supply Chain | 3 | 3 | 6 | 0 | 0 | 33 | 0 | 33 | 1 | 1 | 1 | 0 | 3.3 | Essential for PPU and MaRIE and documentation of corporate knowledge. Phase 1 complete. Currently creating PPU drawings for AT-HVCM.
SCLS-04 | Not Authorized | AIP-44 SCL Cavity Chemistry Facility | No | RAD | SCLS | Kim | GPP | Pending Funding |  | Unscheduled | Capability | 3 | 3 | 3 | 3 | 0 | 33 | 0 | 33 | 1 | 1 | 1 | 0 | 3.3
APBIIS-10 | Authorized | Electron scanner high voltage power supply replacement | No | RAD | APBIIS | Aleksandrov | OIP | Active |  | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 0 | 2.7 | Electrical group is developing new power supply
EERF-06 | Authorized | Development of new High-Power Protection Module | No | RAD | EERF | Champion | OIP | Active |  | Unscheduled | Obsolescence | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 0 | 2.7
EERF-15 | Authorized | Development of the HVCM laminate buss | No | RAD | EERF | Champion | OIP | Active | Modulator Test Facilities | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 0 | 2.7
EERF-26 | Authorized | Redesign HVCM filter to minimize ripple | No | RAD | EERF | Champion | OIP | Pending Resources |  | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 0 | 2.7
EERF-13 | Authorized | Investigate and correct high-power performance of Thales 550 kW klystrons | No | RAD | EERF | Champion | OIP | Pending Resources | RF Test Facility | Unscheduled | Spare | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 0 | 2.4 | Adds ~12 klystrons to spares inventory.
EERF-30 | Authorized | SCL Transmitter Test Rack System | No | RAD | EERF | Champion | OIP | Pending Resources |  | Unscheduled | Low Cost Improvement | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 0 | 2.4 | Off-line test system for SCL Transmitter components and chassis.
MSO-20 | Authorized | Next Generation Primary Foil Changer Mechanism | No | RAD | MSO | Roseberry | OIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 0 | 6 | 3 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 0 | 2.4
MSO-21 | Authorized | Next Generation Secondary Foil Changer Mechanism | No | RAD | MSO | Roseberry | OIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 0 | 6 | 3 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 0 | 2.4
SSG-03 | Authorized | Klystron Gallery Outside Lighting Rework | No | NScD | SITE | McLaughlin | OIP | Pending Funding |  | Unscheduled | Efficiency | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 1 | 2 | 0 | 2.4 | DCN RAD-8300-078 complete which retrofits the existing Klystron Gallery wall mounted lighting fixtures with 35 watt, 277v LED Lamps. Retrofit the west end street lights with direct replacement 110 watt, 480V LED lighting heads. Provide an isolation transformer feeding a new emergency lighting panel to re-feed the above mentioned lighting fixtures in items 1 &2 to prevent ground faults from migrating back to the unit substation.
EERF-31 | Authorized | DTL Iris coupler test cavity | No | RAD | EERF | Champion | OIP | Active |  | Unscheduled | Spare | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 1 | 1 | 0 | 2.1
APBIIS-08 | Authorized | MEBT laser detector replacement | No | RAD | APBIIS | Aleksandrov | OIP | Active |  | Unscheduled | Low Cost Improvement | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 0 | 1.8 | Needs vacuum support for a few hours
APBIIS-13 | Authorized | Ring electron scanner aperture increase | No | RAD | APBIIS | Aleksandrov | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 0 | 1.8 | Need mechanical designer support
EERF-29 | Authorized | Development of new SCL transmitter main control PCB | No | RAD | EERF | Champion | OIP | Pending Resources |  | Unscheduled | Obsolescence | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 0 | 1.8 | Involves controls support. New PCB will be used as a spare for PSS-Main PCB. Tentative prototype delivery of Spring 2017.
MSO-23 | Authorized | LEDP UPGRADE | No | RAD | MSO | Roseberry | OIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 0 | 3 | 0 | 0 | 0 | 9 | 0 | 9 | 1 | 1 | 1 | 0 | 0.9
EERF-25 | Authorized | Completion of 4-way waveguide high power distribution system | No | RAD | EERF | Champion | OIP | Active |  | Unscheduled | Low Cost Improvement | 0 | 0 | 3 | 0 | 0 | 6 | 0 | 6 | 1 | 1 | 1 | 0 | 0.6
MSO-08 | Authorized | Contaminated Relief Valve Test Stand | No | RAD | MSO | Denison | OIP | Pending Resources |  | Unscheduled | Low Cost Improvement | 0 | 0 | 0 | 3 | 0 | 6 | 0 | 6 | 1 | 1 | 1 | 0 | 0.6 | ACTS 0.31205
MSO-41 | Approved | TN Ram Cask Vacuum Upgrade | No | RAD | MSO | Price | OIP | Active |  | Unscheduled | Low Cost Improvement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | This project allows a major time savings for Cask loadout by one day each evolution
SSG-05 | Not Authorized | CRMB Mezzanine Addition | No | RAD | EERF | Champion | OIP | Pending Funding |  | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | Desire to better utilize the high bay space on the ground floor.
MSO-18 | Authorized | Chicane 02 Vacuum Vessel and e-catcher emergency Spare | No | RAD | MSO | Roseberry | OIP | Active |  |  | Spare | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 1 | 4 | 4 | 0 | 16.8
APBIIS-14 | Authorized | Moderator development LDRD | No | RAD | APBIIS | Galambos | OIP | Pending Funding | Beam Test Facility |  | Research and Development | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | Need mechanical and electrical support
APBIIS-15 | Authorized | FODO Line for BTF | No | RAD | APBIIS | Aleksandrov | OIP | Active | Beam Test Facility |  | Research and Development | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 0 | 7.2 | Need mechanical designer support
APBIIS-05 | Authorized | External antenna ion source development | No | RAD | APBIIS | Welton | OIP | Active | Beam Test Facility |  | Research and Development | 9 | 3 | 3 | 0 | 0 | 51 | 0 | 51 | 1 | 1 | 1 | 0 | 5.1
SSG-04 | Approved | Target Building - AHU #9 Needs Re-balanced and re-commissioned and the Controls Upgraded | No | NScD | SITE | McLaughlin | OIP | Active | Now to 2017B |  | Efficiency | 0 | 0 | 3 | 0 | 0 | 6 | 0 | 6 | 2 | 1 | 2 | 0 | 1.2 | Supports COHERENT LDRD Project as well as the current system not performing as designed. Controls Group preparing the DCN. Systematic TAB performed TAB on July 21 and 22nd. Report issued August 2, 2016.

## Color Descriptors
Outage | Activities in process that will complete before the outage | Mandatory Activities - Accelerator/Target | Mandatory Activities - Data Acquisition/Controls | Mandatory Activities - Instrument Upgrades | Mandatory Activities - Other | Concurrent activities for resource planning
2017B
2017C
2018A

## Change Log
Change Number | Change | Date Added | Person
1 | For EERF-14 added note that first article will be installed in 2017A | 2016-09-06
2 | For MSO-14 moved to 2017B, noted that ability to execute in 2017B depends on early availability of AIP funding in FY 2017 | 2016-09-06
3 | Cloned EERF-01, now labeled EERF-01A and EERF-01B to reflect that this work will be done during both 2017A and 2017B | 2016-09-06
4 | For SCLS-02, kept in 2017B and added comment that this is a prerequisite for plasma processing in 2017B | 2016-09-06
5 | Added "Research and Development" and "Capability" to the CATEGORY pull down menu | 2016-09-06
6 | For SCLS-04 changed the Category to Capability | 2016-09-06
7 | For APBIIS-02 changed the Category to Research and Development | 2016-09-06
8 | For SCLS-01 changed the Schedule to Level of Effort | 2016-09-06
9 | For MSO-6 (COHERENT) changed the Project Type to MIE and the Category to Research and Development | 2016-09-06
10 | For APBIIS-14 changed the Category to Research and Development | 2016-09-06
11 | For CON-01 changed the Schedule to Level of Effort | 2016-09-06
12 | Removed EERF-23, MSO-27 and MSO-29 so that there is only one PPU-STS task, all subtasks should be managed within that task and the IWP | 2016-09-06
13 | Added a "Management Status" column to reflect Approved (ready to execute pending CCC review if appropriate), Authorized (design and other preparatory work permitted but no commitment yet to execution), and Not Authorized (no work permitted yet) - we need to discuss | 2016-09-06
14 | Changed nomenclature for outages to YYYYx (months) where x is A, B, C… to identify sequential outage in a given calendar year (YYYY) and "months" represents the months during which the outage occurs in that calendar year. Supports more efficient sorting of outages in sequence. | 2016-09-06
15 | Added crosswalk to FY 2017 NScD Business Plan Commitments in Notes highlighted in red. | 2016-09-06
16 | Numerous edits for science projects to properly identify responsible divisions, groups and owners where known. | 2016-09-06
17 | Scoring updates on certain activities where scores were not entered. | 2016-09-06
18 | Pending action - possible split of SCLS-10 into two outages; need input from SCLS and Controls management. | 2016-09-06
19 | Added SSG-06 and modified comments for SSG-04 per email from McLaughlin. Allocated SSG-06 to 2017B for planning. | 2016-09-23
20 | Changed management status of MSO-30 amd MSO-32 to approved and status to active for 2017A. | 2016-09-23
21 | Added comments to SCLS-10 and MSO-16 at the conclusion of 2016-C. | 2016-10-20 | Jones
22 | Changed status of CON-03 to Approved and color to green | 2016-10-20 | Jones
23 | Changed color of MSO-04 and MSO-05 to light green indicating readiness to proceed to Approved once IRP received and D2O assay results received. | 2016-10-20 | Jones
24 | Updated 2017 Instrument Upgrade Information including new projects with RAD resources per Lacy Jones input | 2016-10-20 | Jones
25 | Updated various lists to include 2018 outages, 2017C outage (end of calendar year) and new project lead names | 2016-10-20 | Jones
26 | Added EERF-32 to incorporate relocation and installation of old RFQ into BTF - placed as level of effort for scheduling. | 2016-10-20 | Jones
27 | Established Baseline October 2016 tab for configuration control for FY2017 | 2016-10-20 | Jones
28 | Modified outage status for MSO-30 and EERF-14 based on input from relevant parties | 2016-10-30 | Jones
29 | Created new Baseline January 2017 in preparation for update. Modified 2017B, 2017C and 2018A-C outage month labels for latest schedules | 2016-01-17 | Jones
30 | SCLS-02 Complete
31 | SCLS-05: note (two cryomodules will be processed in summer 2017. 3-4 additional cryomodules will be processed during the maintenance for IRP change) | 2017-01-26 | Dodson
32 | SCLS-01: now the status is ‘Active’ | 2017-01-26 | Dodson
33 | SCLS-03: note (The final connection requires SCLS-08) | 2017-01-26 | Dodson
34 | SCLS-08: note (engineering analysis is ongoing for a cheaper solution) | 2017-01-26 | Dodson
35 | SCLS-10 Completion to Summer Shudown 2017B | 2017-01-26 | Dodson
36 | MSO-03 Water Mist System Restoration. Complete | 2017-01-26 | Dodson
37 | MSO-04 IRP Replacement. Move to 2018C outage. | 2017-02-10 | Dodson
38 | MSO-05 Heavy Water Conversion. Move to the 2018C outage. | 2017-02-10 | Dodson
39 | MSO-06 COHERENT Experiment. Complete (but frequent changes are still being supported). | 2017-02-10 | Dodson
40 | MSO-07 Helium gas injection. Move to the 2017C outage. | 2017-02-10 | Dodson
41 | MSO-08 Contaminated Relief Valve Test Stand. Indefinite hold. | 2017-02-10 | Dodson
42 | MSO-14 AIP35 Warm LINAC Vacuum Upgrade (CCL1&2). Move to the 2017B outage. | 2017-02-10 | Dodson
43 | MSO-16 Heavy Water Receipt and Sampling. Complete. | 2017-02-10 | Dodson
44 | MSO-17 Linac Plug Door Replacement. Move to the 2018C outage. | 2017-02-10 | Dodson
45 | MSO-18 Chicane 02 Vacuum Vessel and e-Catcher Emergency Spare. Move to the 2017B outage. | 2017-02-10 | Dodson
36 | MSO-25 Remote Auto-fill of Collimator Cooling. Indefinite hold. | 2017-02-10 | Dodson
37 | MSO-30 Replace Obsolete MKS Gauge Controllers. Move to the 2017B outage. | 2017-02-10 | Dodson
48 | MSO-31 Add RTBT Turbo. Move to the 2017B outage. | 2017-02-10 | Dodson
49 | MSO-32 LEBT Foreline Valves Controls Reconfiguration. Complete. | 2017-02-10 | Dodson
50 | MSO-33 Addition of RTDs to Warm LINAC Valves. Complete. | 2017-02-10 | Dodson
51 | INS-07SEQUOIA Vacuum Upgrade. Move to the 2018C outage. | 2017-02-10 | Dodson
52 | Modified list sources for Non-Outage Schedule and Outage Schedule to reflect change in approach | 2017-02-27 | Jones
53 | MSO-42 Added, RFTF DIW & Glycol Instrumentation Upgrade | 2017-02-28 | Dodson/Baumgartner
54 | Updated IDAC-04 to reflect re-scheduling to 2018A per S. Hartman | 2017-03-01 | Jones
55 | Added IDAC-07, VULCAN DAQ Upgrade with attributes similar to IDAC-04 but scheduled in 2017B per S. Hartman | 2017-03-01 | Jones
56 | Changed status of IDAC-05, 06 and 07 to Active to identify preparation path to 2017B execution | 2017-03-01 | Jones
57 | Per Price note of 02/28/17 changed outage for INS-01 to 2018B | 2017-03-01 | Jones
58 | Per Price note of 02/28/17 removed outage for INS-05 to reflect planned completion of POWGEN Phase I upgrade prior to 2017B | 2017-03-01 | Jones
59 | Per Price note of 02/28/17 changed outage for INS-07 to 2018A with pre-outage work from now through 2018A | 2017-03-01 | Jones
60 | Per Price note of 02/28/17 changed outage for INS-02 to 2018B with pre-outage work from now through 2018B | 2017-03-01 | Jones
61 | Per Price note of 02/28/17 changed outage for INS-13 to 2018B, Management Status to Approved, Status to Active, Now through 2017B | 2017-03-01 | Jones
62 | Removed outage identifier for MSO-18 | 2017-03-01 | Jones
63 | Split SCLS-05 into A and B for 2017B and 2018A respectively to reflect current plasma processing plan | 2017-03-01 | Jones
64 | Per Update from Cross changed INS-01 and INS-02 to now be planned for 2017B (subject to confirmation) | 2017-03-01 | Jones
65 | Modified EERF-20 to remove outage schedule (all installation done, testing underway with beam) | 2017-03-03 | Jones
66 | Worked with Glen Johns to resolve discrepancies in notes and restore to proper alignment | 2017-03-03 | Jones/Johns
67 | Added coloration (see separate tab for descriptors) to identify mandatory work for different outages and concurrent planning activities | 2017-03-03 | Jones
68 | Changed status of IDAC-04 to Active, Added IDAC-08,09,10 consistent with IDAC-05 but working through 2018A per Hartman | 2017-03-06 | Jones
69 | Changed status of MSO-38 to Active and modified to be performed during 2018A with work leading up to 2018A | 2017-03-06 | Jones
70 | Changed notes for EERF-09, EERF-14 and EERF-31; removed EERF-08 per Mark Champion | 2017-03-06 | Jones
71 | Moved MSO-10 to 2018A and added note that it is linked to INS-07 - per B. Cross | 2017-03-06 | Jones
72 | Removed original version tab for Baseline January 2017 to avoid confusion | 2017-03-06 | Jones
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128

## List Sources
RiskType
Rep | Reputation | Adversely affects the reputation of SNS leading to either decreased user demand and/or loss of funding and/or decrease in sponsor confidence
Fin | Financial | Decreases the SNS budget leading to either reduced operations or quality of user service (independent of short term/long term)
Oper | Operational | Affects the ability to run SNS either for the number of scheduled hours or with a reduction in quality of user services (neutron flux, sample environment, detector coverage, etc.)
Rep & Fin | Reputation and Financial | Combination of Reputation and Financial
Rep & Oper | Reputation and Operational | Combination of Reputation and Operational
Fin & Oper | Financial and Operational | Combination of Financial and Operational
Rep, Fin and Oper | Reputation, Financial and Operational | Combination of All Three
RiskOwner
Langan | ALD
Tennant | Chief Scientist
Schrof | Scientific Program Office
Vogel | DOM
Abercrombie | ISD
Bras | BSMD
Ibberson | CEMD
Jones | RAD
Nagler | QCMD
Powers | RRD
Proffen | NDAVD
Galambos | PPU
Galambos | STS
Hickey | FIN
Hebert | HR
Galambos | APBIIS
Champion | EERF
Baumgartner | MSO
Kim | SCLS
Johns | OPS
White | CON
Hartman | IDAC
McKenzie | FAC
McLaughlin | SITE
Rowland | ESHQ
DirDiv
NScD | Directorate Office
ISD | Instrument and Source Division
CEMD | Chemical and Engineering Materials Division
RAD | Research Accelerator Division
QCMD | Quantum Condensed Matter Division
RRD | Research Reactors Division
NDAVD | Neutron Data Analysis and Visualization Division
BSMD | Biology and Soft Matter Division
DOO | Directorate Operations Office
PPU | PPU Project Office
STS | STS Project Office
SPSO | Scientific and Program Services Office
Group
APBIIS | Accelerator Physics, Beam Instrumentation and Ion Source
EERF | Electrical Engineering and RF
MSO | Mechanical Systems and Operations
SCLS | Superconducting Linac Systems
OPS | Operations
CON | Control Systems
IDAC | Instrument Data Acquisition and Control
FAC | Facilities Management
SITE | Site Services
ESHQ | Environment, Safety, Health and Quality
SNSINST | SNS Instrument Operations
HFIRINST | HFIR Instrument Operations
SNSENG | SNS Instrument Engineering
HFIRENG | HFIR Instrument Engineering
SE | Sample Environment
IPD | Instrument Projects and Development
SDEA | Source Development and Engineering Analysis
CFQA | Compliance, Fabrication, and Quality Assurance
PMOA | Project Management and Operations Analysis
ENENV | Energy and the Environment
BBS | Biology and Biomedical Sciences
SDSM | Structure and Dynamics of Soft Matter
CHEMCRYS | Chemical Crystallography
ADVDIFF | Advanced Diffraction
ENGMAT | Engineering Materials
SPEC | Spectroscopy
TECHADV | NDAV Technology Advancement (Matrix)
SDA | Scientific Data Analysis
CAMM | Center for Accelerating Materials Modeling
TAX | Triple-Axis Spectroscopy
TFN | Thin Films and Nanostructures
SOM | Structure of Matter
TOF | Time-of-Flight Spectroscopy
USER | User Program
COMM | Communications and Outreach
STS | Science and Technology Systems
DCRM | Document Control and Records Management (Deployed)
DIV | Division Office
PPU | PPU Project
STS | STS Project
PROC | Procurement (Deployed)
Score
0 | No criteria met
3 | One criterion met
6 | Two criteria met
9 | Three or more criteria met
ProjectType | ProbConsScore
AIP | 1
GPP | 2
IGPP | 3
OIP | 4
Facility Upgrade | 5
Instrument Upgrade
MIE | Active
OIPsubtype | Pending Safety Basis
Spare | Design
Research and Development | Pending Funding
Capability | Pending Resources
Facility Upgrade | Pending Planning
Supply Chain | Complete
Obsolescence | On Hold
Low Cost Improvement
Safety
Efficiency | 2016C (October) |  | #NAME?
Unscheduled
2017A (January)
ProjectLead | 2017B (May-June)
Abercrombie | 2017C (October)
Abernathy | 2018A (December-April)
Agrawal | 2018B (July-August)
Aleksandrov | 2018C (November-January)
An | 2019A (April)
Anderson (DE) | 2019B (July-August)
Baumgartner | 2019C (November-January)
Bras | 2020A (April)
Bullman | 2020B (July-August)
Cagley | 2020C (November-January)
Cao
Champion | Now to 2017A
Chi | Now to 2017B
Cousineau | Now to 2017C
Crofford | Now to 2018A
Curry | Now to 2018B
Denison | Now to 2018C
Dodson (G) | Now to 2019A
Doleans | Now to 2019B
Ehlers | Now to 2019C
Everett | Now to 2020A
Fitzsimmons | Now to 2020B
Galambos | Now to 2020C
Hartman | Level of Effort
Hebert | RF Test Facility
Heller | Modulator Test Facilities
Herwig | Beam Test Facility
Hickey | Long Lead Procurements
Howell | Unscheduled
Huq | Not Applicable
Ibberson
Jacobs
Johns
Jones (K) | Approved
Jones (L) | Authorized
Kang | Not Authorized
Kasemir
Kim
Kohl
Kristy
Langan
Longcoy | No
Magda | Yes
Mahoney
McKenzie | 0
McLaughlin | 10
Middendorf | 50
Moss | 100
Nagler
Norman
Norris
Payzant
Piller
Plum
Pope
Powers
Price
Proffen
Roseberry
Rowland
Saethre
Saunders
Schrof
Schubert
Sinclair
Smith, C. Craig
Stockli
Stockton
Stone
Strong
Tennant
Tian
Trotter (S)
Tucker
Tulk
Vogel
Webb
Welton
White
Williams (D)
Winn
Ye
TBD
Placeholder

## Completed or Removed Projects
RAD Global Priorities
[12 empty] | Criterion 1 | Criterion 2 | Criterion 3 | Criterion 4 | Criterion 5 | Criteria Scores |  |  | Probability | Consequence | Risk | Safety | Overall Impact | Notes
Criterion: | [11 empty] | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects |  |  |  | Estimated Frequency of Downtime Event if Project not Undertaken | Estimated Duration of Downtime Event if Project Not Undertaken | Product of Probability and Consequence | Personnel Safety
Criterion Scope: | [11 empty] | • >5000 hours of scheduled neutron production • 100% predictability • ≥90% reliability against schedule • minimize down times ≥3 hours | • operate at 1.4 MW • provide additional margin for 1.4 MW operation • support progress toward 2 MW operation for FTS | • enhance the capability of more than one neutron scattering instrument • enhance the capability of the neutron source to support all instruments • advance accelerator science or technology with possible application the neutron source | • Technical action item from an external review (e.g. NAB, DOE, AAC, ASRC) • Technical action item from an internal review or assessment • Technical action item from an operational event or a regulatory requirement • PEMP or other primary sponsor commitment | • Project is on approved current year science priority list but not time critical, LDRD or externally funded limited term • Project is on approved science priority list with specific actions to address • Project is on science priority list for out year consideration • Project is not on science priority list or not considered |  |  |  | • Once a week • Once a month • Once a quarter • Once a year • Once every 2 years or longer | • One year or more • 3 months to one year • 1 to 3 months • 1 week to 1 month • 1 day to 1 week |  | Risk of injury of varying severity or of fatality to workers
Scoring Rules for each Criterion: | [11 empty] | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If not on list score 0; if out year consideration score 3; if planning stage score 6; if current year execution score 9 |  |  |  | If once a week, score 5; if once a month score 4; if once a quarter score 3; if once a year score 2; if once every 2 years or longer, or no likely downtime score 1. | If one year or more score 5; if 3 months to 1 year score 4; if 1 to 3 months score 3; if 1 week to 1 month score 2; if 1 day to 1 week score 1 |  | If No Risk of Injury to Personnel score a 1; if possible recordable injury score 10; if possible DART case score 50; if possible fatality score 100
Guidance: | [11 empty] | Evaluate whether the project directly affects the ability of the facility to meet the four scope elements listed above and score accordingly. | Evaluate whether the project will affect operating power capability according to the criteria and score accordingly. | Evaluate the project to determine whether it enhances capability of more than one instrument, or the accelerator, or is a funded external project and score accordingly. | Determine whether the project must be done in response to one or more external drivers, and score accordingly. | Determine the status of the project on the current approved instrument upgrade plan and score accordingly. |  |  |  | Perform a qualitative assessment of the frequency of system-related downtime events if the project is not performed. | Perform a qualitative assessment of the duration of the downtime for each occurrence if the project is not performed |  | Perform a qualitative assessment of the impact that not undertaking the activity will have on personnel safety
Weighting Factor: | [11 empty] | 4 | 3 | 2 | 2 | 8 |  |  |  | 1 | 1 |  | 10
Project Identifier | Management Status | Project | Commitment (PEMP or Business Plan) | Owning Division | Owning Group | Project Lead | Project Type | Status | Non-Outage Schedule | Outage Schedule | Category | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects | Weighted Score (Criteria 1-4) | Science Score (Criterion 5) | Total Score (Criteria 1-5) | Probability (1-5) | Consequence (1-5) | Risk (1-25) | Risk of Injury to Personnel | Overall Impact | Notes
APBIIS-01 |  | Laser Stripping Experiment and Grant deliverables |  | RAD | APBIIS | Cousineau | OIP |  |  |  |  | 0 | 3 | 0 | 0 | 9 | #REF! | #REF! | #REF! | 1 | 1 | 1 | 0 | #REF!
APBIIS-07 |  | AIP-30 ITSF construction |  | RAD | APBIIS | Aleksandrov | AIP |  |  |  |  | 9 | 9 | 9 | 0 | 0 | #REF! | #REF! | #REF! | 1 | 4 | 4 | 0 | #REF! | Needed to test new RFQ.
APBIIS-09 |  | SCL laser wire improvement & alignment |  | RAD | APBIIS | Aleksandrov | OIP |  |  |  | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | #REF! | #REF! | #REF! | 1 | 1 | 1 | 0 | #REF! | Need support to pull one or two cables
CON-02 |  | Isolate Klystron Gallery PPS Cabinet |  | RAD | CON | White | OIP |  |  |  | Efficiency | 9 | 3 | 0 | 9 | 0 | #REF! | #REF! | #REF! | 1 | 3 | 3 | 0 | #REF!
CON-05 |  | Reconfigure Controls Chassis in BBB |  | RAD | CON | Curry | OIP |  |  |  |  | 9 | 3 | 0 | 0 | 0 | #REF! | #REF! | #REF! | 3 | 1 | 3 | 0 | #REF!
CON-06 |  | Modify JT valve controls for manual mode |  | RAD | CON | Strong | OIP |  |  |  |  | 9 | 3 | 0 | 0 | 0 | #REF! | #REF! | #REF! | 2 | 1 | 2 | 0 | #REF!
EERF-24 |  | Install two Thales klystrons in DTL |  | RAD | EERF | Champion | OIP |  |  |  | Spare | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0
IDAC-01 |  | POWGEN DAQ/Controls Upgrade |  | RAD | IDAC | Hartman | OIP |  |  |  | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6 | Completed
IDAC-02 |  | NOMAD DAQ/Controls Upgrade |  | RAD | IDAC | Hartman | OIP |  |  |  | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6 | Completed
MSO-11 |  | BL17 Vacuum Upgrade |  | RAD | MSO | Price | OIP | Active |  | 2017B (April-July) | Low Cost Improvement | 0 | 0 | 0 | 0 | 6 | 0 | 48 | 48 | 2 | 1 | 2 | 0 | 9.6 | Removed in lieu of INS-07.
APBIIS-03 |  | Replace chicane #2 vac. ch. (Also MSO-2) |  | RAD | APBIIS | Roseberry | OIP |  |  |  |  | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 1 | 4 | 4 | 0 | 25.2
MSO-29 |  | PPU / STSUtility Systems Design |  | RAD | MSO | Jacobs | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | [5 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0 | Consolidated to single PPU-STS activity
EERF-23 |  | PPU deliverables |  | RAD | EERF | Champion | MIE | Active |  | Unscheduled | Low Cost Improvement | 0 | 6 | 3 | 3 | 0 | 30 | 0 | 30 | 1 | 1 | 1 | 0 | 3 | Consolidated to single PPU-STS activity
MSO-27 |  | PPU / STS Klystron Gallery CREO Model |  | RAD | MSO | Roseberry | OIP | Pending Funding |  | Unscheduled | Low Cost Improvement | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 4 | 4 | 0 | 8.4 | Consolidated to single PPU-STS activity
MSO-09 |  | LEDP Isolation Valve Improvements |  | RAD | MSO | Price | OIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 2 | 4 | 0 | 4.8
SCLS-02 | Approved | Plasma Hardware for Multiple Cryomodule Deployment | Yes | RAD | SCLS | Kim | OIP | Complete |  | 2017B (May-June) | Efficiency | 3 | 9 | 3 | 6 | 0 | #REF! | #REF! | #REF! | 1 | 1 | 1 | 0 | #REF! | FY2017 Business Plan Objective 2.c.2. Required to support SCLS-05 during 2017B.
MSO-03 | Authorized | Water Mist System Restoration | No | RAD | MSO | Denison | OIP | Complete |  | Unscheduled | Low Cost Improvement | 0 | 0 | 0 | 6 | 0 | #REF! | #REF! | #REF! | 1 | 1 | 1 | 0 | #REF!
MSO-06 | Authorized | COHERENT Experiment | No | NScD | FAC | Vogel | MIE | Complete |  | Unscheduled | Research and Development | 0 | 0 | 3 | 0 | 9 | #REF! | #REF! | #REF! | 1 | 1 | 1 | 0 | #REF!
MSO-16 | Approved | Heavy Water Receipt and Sampling | Yes | RAD | MSO | Jacobs | OIP | Complete |  | 2016C (October) | Low Cost Improvement | 0 | 0 | 6 | 3 | 3 | #REF! | #REF! | #REF! | 1 | 1 | 1 | 0 | #REF! | FY 2017 Business Plan Objective 2.d.4. Will begin before 2016C, and conclude after end of 2016C.
MSO-32 | Approved | Reconfigure LEBT Foreline Valves and Controls | No | RAD | MSO | Price | OIP | Complete |  | 2017A (January) | Low Cost Improvement | 6 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | 2 | 1 | 2 | 0 | 4.8
MSO-33 | Authorized | Add Temperature Measurement to Warm Linac SGVs | No | RAD | MSO | Price | OIP | Complete |  | Unscheduled | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | 2 | 1 | 2 | 0 | 2.4
EERF-01A | Approved | AIP-34 HVCM Controller Upgrade | Yes | RAD | EERF | Champion | AIP | Complete |  | 2017A (January) | Obsolescence | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 3 | 1 | 3 | 0 | 19.8 | FY2017 Business Plan Objectives 2.c.2 and 3.c.
EERF-03 | Authorized | JEMA Modulator testing | No | RAD | EERF | Champion | OIP | Complete |  | Unscheduled | Supply Chain | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 1 | 1 | 0 | 2.1 | CRADA with ESS-Bilbao.
IDAC-03 | Approved | MANDI DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Complete |  | 2017A (January) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 0 | 33.6
EERF-08 | Authorized | Improve cooling of equipment racks in klystron gallery | No | RAD | EERF | Champion | OIP | Pending Planning |  | Unscheduled | Low Cost Improvement | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 1 | 2 | 0 | 7.2 | McLaughlin has a proposal.

## Baseline April 2016
RAD Global Priorities
[7 empty] | Criterion 1 | Criterion 2 | Criterion 3 | Criterion 4 | Criterion 5 | Criteria Scores |  |  | Probability | Consequence | Risk | Overall Impact | Notes
Criterion: | [6 empty] | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects |  |  |  | Estimated Frequency of Downtime Event if Project not Undertaken | Estimated Duration of Downtime Event if Project Not Undertaken | Product of Probability and Consequence
Criterion Scope: | [6 empty] | • >5000 hours of scheduled neutron production • 100% predictability • ≥90% reliability against schedule • minimize down times ≥3 hours | • operate at 1.4 MW • provide additional margin for 1.4 MW operation • support progress toward 2 MW operation for FTS | • enhance the capability of more than one neutron scattering instrument • enhance the capability of the neutron source to support all instruments • advance accelerator science or technology with possible application the neutron source | • Technical action item from an external review (e.g. NAB, DOE, AAC, ASRC) • Technical action item from an internal review or assessment • Technical action item from an operational event or a regulatory requirement • PEMP or other primary sponsor commitment | • Project is on approved current year science priority list, LDRD or externally funded limited term • Project is on approved science priority list in planning stage with execution the following year • Project is on science priority list for out year consideration • Project is not on science priority list |  |  |  | • Once a week • Once a month • Once a quarter • Once a year • Once every 2 years or longer | • One year or more • 3 months to one year • 1 to 3 months • 1 week to 1 month • 1 day to 1 week
Scoring Rules for each Criterion: | [6 empty] | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If not on list score 0; if out year consideration score 3; if planning stage score 6; if current year execution score 9 |  |  |  | If once a week, score 5; if once a month score 4; if once a quarter score 3; if once a year score 2; if once every 2 years or longer, or no likely downtime score 1. | If one year or more score 5; if 3 months to 1 year score 4; if 1 to 3 months score 3; if 1 week to 1 month score 2; if 1 day to 1 week score 1
Guidance: | [6 empty] | Evaluate whether the project directly affects the ability of the facility to meet the four scope elements listed above and score accordingly. | Evaluate whether the project will affect operating power capability according to the criteria and score accordingly. | Evaluate the project to determine whether it enhances capability of more than one instrument, or the accelerator, or is a funded external project and score accordingly. | Determine whether the project must be done in response to one or more external drivers, and score accordingly. | Determine the status of the project on the current approved instrument upgrade plan and score accordingly. |  |  |  | Perform a qualitative assessment of the frequency of system-related downtime events if the project is not performed. | Perform a qualitative assessment of the duration of the downtime for each occurrence if the project is not performed
Weighting Factor: | [6 empty] | 4 | 3 | 2 | 2 | 8 |  |  |  | 1 | 1
Project Identifier | Project | Owning Division | Owning Group | Project Lead | Project Type | Category | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects | Weighted Score (Criteria 1-4) | Science Score (Criterion 5) | Total Score (Criteria 1-5) | Probability (1-5) | Consequence (1-5) | Risk (1-25) | Overall Impact | Notes
APBIIS-01 | Laser Stripping Experiment and Grant deliverables | RAD | APBIIS | Cousineau | OIP |  | 0 | 3 | 0 | 0 | 9 | 9 | 72 | 81 | 1 | 1 | 1 | 8.1 |  | 1
APBIIS-02 | 6D phase space grant | RAD | APBIIS | Cousineau | OIP |  | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | Need mechanical and electrical support | 2
APBIIS-03 | Replace chicane #2 vac. ch. (Also MSO-2) | RAD | APBIIS | Roseberry | OIP |  | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 1 | 4 | 4 | 25.2 |  | 3
APBIIS-05 | External antenna ion source development | RAD | APBIIS | Welton | OIP |  | 9 | 3 | 3 | 0 | 0 | 51 | 0 | 51 | 1 | 1 | 1 | 5.1 |  | 6
APBIIS-06 | AIP-37 Beam Instrumentation Infrastructure Improvements | RAD | APBIIS | Aleksandrov | OIP | Obsolescence | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 4 | 8 | 9.6 | Linac BPM upgrade, Ring BPM upgrade, BLM upgrade | 7
APBIIS-07 | AIP-30 ITSF construction | RAD | APBIIS | Aleksandrov | AIP |  | 9 | 9 | 9 | 0 | 0 | 81 | 0 | 81 | 1 | 4 | 4 | 32.4 | Needed to test new RFQ. | 8
APBIIS-08 | MEBT laser detector replacement | RAD | APBIIS | Aleksandrov | OIP | Low Cost Improvement | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 1.8 | Needs vacuum support for a few hours
APBIIS-09 | SCL laser wire improvement & alignment | RAD | APBIIS | Aleksandrov | OIP | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7 | Need support to pull one or two cables
APBIIS-10 | Electron scanner high voltage power supply replacement | RAD | APBIIS | Aleksandrov | OIP | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7 | Electrical group is developing new power supply
APBIIS-11 | RTBT harp electronics | RAD | APBIIS | Aleksandrov | OIP | Obsolescence | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 2 | 4 | 8 | 21.6 | Upgrade and spare for existing electronics
APBIIS-12 | Injection foil video improvement | RAD | APBIIS | Aleksandrov | OIP | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 3 | 1 | 3 | 8.1 | Need mechanical designer support
APBIIS-13 | Ring electron scanner aperture increase | RAD | APBIIS | Aleksandrov | OIP | Low Cost Improvement | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 1.8 | Need mechanical designer support
APBIIS-14 | Moderator development LDRD | RAD | APBIIS | Galambos | OIP |  | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | Need mechanical and electrical support
CON-01 | AIP-39 Machine Protection System Improvements | RAD | CON | White | AIP |  | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 1 | 3 | 3 | 18.9
CON-02 | Isolate Klystron Gallery PPS Cabinet | RAD | CON | White | OIP | Efficiency | 9 | 3 | 0 | 9 | 0 | 63 | 0 | 63 | 1 | 3 | 3 | 18.9
CON-03 | Install high power shutters DTL1/2 waveguide | RAD | CON | White | OIP | Efficiency | 9 | 3 | 3 | 3 | 0 | 57 | 0 | 57 | 3 | 1 | 3 | 17.1
CON-04 | ReplacePLCs/Panelview for Target | RAD | CON | Strong | OIP |  | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 1 | 1 | 4.5 | Includes correcting initialization routines
CON-05 | Reconfigure Controls Chassis in BBB | RAD | CON | Curry | OIP |  | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 3 | 1 | 3 | 13.5
CON-06 | Modify JT valve controls for manual mode | RAD | CON | Strong | OIP |  | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 2 | 1 | 2 | 9
CON-07 | Replacement for PSC | RAD | CON | Curry | OIP |  | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 1 | 1 | 1 | 3.3
EERF-01 | AIP-34 HVCM Controller Upgrade | RAD | EERF | Champion | AIP | Obsolescence | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 3 | 1 | 3 | 19.8
EERF-02 | HVCM Alternate Topology Modulator development | RAD | EERF | Champion | OIP | Low Cost Improvement | 6 | 6 | 6 | 0 | 0 | 54 | 0 | 54 | 1 | 1 | 1 | 5.4
EERF-03 | JEMA Modulator testing | RAD | EERF | Champion | OIP | Supply Chain | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 1 | 1 | 2.1 | CRADA with ESS-Bilbao.
EERF-04 | Develop thryatron replacement for extraction kicker PFNs | RAD | EERF | Champion | OIP | Low Cost Improvement | 3 | 6 | 6 | 0 | 0 | 42 | 0 | 42 | 1 | 1 | 1 | 4.2
EERF-05 | Comprehensive update of the HVCM design drawings including red line capture | RAD | EERF | Champion | OIP | Supply Chain | 3 | 3 | 6 | 0 | 0 | 33 | 0 | 33 | 1 | 1 | 1 | 3.3 | Essential for PPU and MaRIE and documentation of corporate knowledge.
EERF-06 | Development of new High-Power Protection Module | RAD | EERF | Champion | OIP | Obsolescence | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7 |  | 4
EERF-07 | Development of new LLRF system | RAD | EERF | Champion | OIP | Low Cost Improvement | 3 | 6 | 3 | 0 | 0 | 36 | 0 | 36 | 1 | 1 | 1 | 3.6 | Essential for PPU. | 5
EERF-08 | Improve cooling of equipment racks in klystron gallery | RAD | EERF | Champion | OIP | Low Cost Improvement | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 1 | 2 | 7.2 | McLaughlin has a proposal.
EERF-09 | Procure spare circulators | RAD | EERF | Champion | OIP | Spare | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 5 | 10 | 36
EERF-10 | Procure spare klystrons | RAD | EERF | Champion | OIP | Spare | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 5 | 5 | 22.5
EERF-11 | Develop alternative supply chain for 2.5 and 5.0 MW klystrons | RAD | EERF | Champion | OIP | Supply Chain | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 5 | 5 | 22.5
EERF-12 | Installation of new RFQ at Front-End building | RAD | EERF | Champion | OIP | Low Cost Improvement | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 2 | 4 | 8 | 52.8
EERF-13 | Investigate and correct high-power performance of Thales 550 kW klystrons | RAD | EERF | Champion | OIP | Spare | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 2.4 | Adds ~12 klystrons to spares inventory.
EERF-14 | Develop alternative RF-Vacuum window source for DTL and CCL | RAD | EERF | Champion | OIP | Spare | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 2 | 4 | 8 | 33.6 | Continuation of work with Mega Inc.
EERF-15 | Development of the HVCM laminate buss | RAD | EERF | Champion | OIP | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7
EERF-16 | Develop alternative source of HVCM boost capacitors | RAD | EERF | Champion | OIP | Supply Chain | 6 | 6 | 3 | 3 | 0 | 54 | 0 | 54 | 2 | 1 | 2 | 10.8
EERF-17 | HVCM IGBT replacement | RAD | EERF | Champion | OIP | Obsolescence | 9 | 6 | 3 | 0 | 0 | 60 | 0 | 60 | 4 | 1 | 4 | 24
EERF-18 | AIP-46 Linac Quad power supply standardization | RAD | EERF | Champion | AIP | Low Cost Improvement | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 1 | 2 | 7.2
EERF-19 | PSI upgrade | RAD | EERF | Champion | OIP | Obsolescence | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 3 | 1 | 3 | 9.9
EERF-20 | LEBT smart chopping | RAD | EERF | Champion | OIP | Low Cost Improvement | 6 | 6 | 6 | 0 | 0 | 54 | 0 | 54 | 1 | 1 | 1 | 5.4
EERF-21 | Procure spare substation transformers | RAD | EERF | Champion | OIP | Spare | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 2 | 1 | 2 | 4.8
EERF-22 | Replace RNSS-2 switch with a remotely operated switch | RAD | EERF | Champion | OIP | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 1 | 1 | 1 | 1.2
EERF-23 | PPU deliverables | RAD | EERF | Champion | MIE | Low Cost Improvement | 0 | 6 | 3 | 3 | 0 | 30 | 0 | 30 | 1 | 1 | 1 | 3
EERF-24 | Install two Thales klystrons in DTL | RAD | EERF | Champion | OIP | Spare | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 1 | 1 | 1 | 3.6
IDAC-01 | POWGEN DAQ/Controls Upgrade | RAD | IDAC | Hartman | OIP | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 33.6
IDAC-02 | NOMAD DAQ/Controls Upgrade | RAD | IDAC | Hartman | OIP | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 33.6
MSO-01 | Primary Foil Changer Spare & Test Stand | RAD | MSO | Baumgartner | OIP | Spare | 6 | 9 | 0 | 0 | 0 | 51 | 0 | 51 | 3 | 1 | 3 | 15.3
MSO-03 | Water Mist System Restoration | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 0 | 0 | 0 | 6 | 0 | 12 | 0 | 12 | 1 | 1 | 1 | 1.2
MSO-04 | IRP Replacement | RAD | MSO | Baumgartner | OIP | Efficiency | 9 | 0 | 6 | 3 | 0 | 54 | 0 | 54 | 2 | 5 | 10 | 54
MSO-05 | HWS #4 Heavy Water Conversion | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 0 | 0 | 6 | 3 | 3 | 18 | 24 | 42 | 1 | 1 | 1 | 4.2
MSO-06 | COHERENT Experiment | NScD | FAC | Vogel |  |  | 0 | 0 | 3 | 0 | 9 | 6 | 72 | 78 | 1 | 1 | 1 | 7.8
MSO-07 | Helium Gas Injection | ISD | SDEA | Baumgartner | OIP | Low Cost Improvement | 9 | 9 | 3 | 6 | 0 | 81 | 0 | 81 | 3 | 2 | 6 | 48.6
MSO-08 | Contaminated Relief Valve Test Stand | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 0 | 0 | 0 | 3 | 0 | 6 | 0 | 6 | 1 | 1 | 1 | 0.6
MSO-09 | LEDP Isolation Valve Improvements | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 2 | 4 | 4.8
MSO-10 | BL17 SET Turbo Integration | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2
MSO-11 | BL17 Vacuum Upgrade | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 0 | 0 | 0 | 0 | 6 | 0 | 48 | 48 | 2 | 1 | 2 | 9.6
MSO-12 | RF Window "Post-Conditioned" Vacuum System | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 2 | 1 | 2 | 6 | ACTS 0.31205
MSO-13 | Servo-Manipulator Replacement | RAD | MSO | Baumgartner | AIP | Obsolescence | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 1 | 1 | 1 | 3
MSO-14 | AIP-35 Warm Linac Vacuum Upgrade | RAD | MSO | Baumgartner | AIP | Obsolescence | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 5 | 1 | 5 | 21
MSO-15 | AIP-36 HVCM Cooling Upgrade | RAD | MSO | Baumgartner | AIP | Low Cost Improvement | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 3 | 1 | 3 | 18.9
MSO-16 | Heavy Water Receipt and Sampling | RAD | MSO | Baumgartner | OIP | Low Cost Improvement | 0 | 0 | 6 | 3 | 3 | 18 | 24 | 42 | 1 | 1 | 1 | 4.2
SCLS-01 | Medium Beta Spare Cryomodule | RAD | SCLS | Kim | OIP | Spare | 9 | 9 | 0 | 3 | 0 | 69 | 0 | 69 | 2 | 2 | 4 | 27.6
SCLS-02 | Plasma Hardware for Multiple Cryomodule Deployment | RAD | SCLS | Kim | OIP | Efficiency | 3 | 9 | 3 | 6 | 0 | 57 | 0 | 57 | 1 | 1 | 1 | 5.7
SCLS-03 | Spare Carbon Bed | RAD | SCLS | Kim | OIP | Spare | 9 | 0 | 0 | 6 | 0 | 48 | 0 | 48 | 1 | 4 | 4 | 19.2
SCLS-04 | AIP-44 SCL Cavity Chemistry Facility | RAD | SCLS | Kim | GPP |  | 3 | 3 | 3 | 3 | 0 | 33 | 0 | 33 | 1 | 1 | 1 | 3.3
SSG-01 | RAD Shop & Assembly Building | NScD | SITE | McLaughlin | GPP |  | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | Conceptual effort needed to establish site and funding needs
SSG-02 | Klystron Gallery HVAC System Improvements | RAD | SITE | McLaughlin | OIP | Efficiency | 3 | 0 | 0 | 3 | 0 | 18 | 0 | 18 | 2 | 1 | 2 | 3.6 | On-going issue with air circulation for cooling the instrument racks. Needs support from CUB (chilled water) and Controls Group.
SSG-03 | Klystron Gallery Outside Lighting Rework | NScD | SITE | McLaughlin | OIP | Efficiency | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 1 | 2 | 2.4 | DCN RAD-8300-078 retrofit the existing Klystron Gallery wall mounted lighting fixtures with 35 watt, 277v LED Lamps. Retrofit the west end street lights with direct replacement 110 watt, 480V LED lighting heads. Provide an isolation transformer feeding a new emergency lighting panel to re-feed the above mentioned lighting fixtures in items 1 &2 to prevent ground faults from migrating back to the unit substation.
SSG-04 | Target Building - AHU #9 Needs Re-balanced and re-commissioned and the Controls Upgraded | NScD | SITE | McLaughlin | OIP | Efficiency | 0 | 0 | 3 | 0 | 0 | 6 | 0 | 6 | 2 | 1 | 2 | 1.2 | Supports COHERENT LDRD Project as well as the current system not performing as designed. Needs support from Controls Group.
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0 |  |  | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0

## Baseline October 2016
RAD Global Priorities
[11 empty] | Criterion 1 | Criterion 2 | Criterion 3 | Criterion 4 | Criterion 5 | Criteria Scores |  |  | Probability | Consequence | Risk | Overall Impact | Notes
Criterion: | [10 empty] | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects |  |  |  | Estimated Frequency of Downtime Event if Project not Undertaken | Estimated Duration of Downtime Event if Project Not Undertaken | Product of Probability and Consequence
Criterion Scope: | [10 empty] | • >5000 hours of scheduled neutron production • 100% predictability • ≥90% reliability against schedule • minimize down times ≥3 hours | • operate at 1.4 MW • provide additional margin for 1.4 MW operation • support progress toward 2 MW operation for FTS | • enhance the capability of more than one neutron scattering instrument • enhance the capability of the neutron source to support all instruments • advance accelerator science or technology with possible application the neutron source | • Technical action item from an external review (e.g. NAB, DOE, AAC, ASRC) • Technical action item from an internal review or assessment • Technical action item from an operational event or a regulatory requirement • PEMP or other primary sponsor commitment | • Project is on approved current year science priority list but not time critical, LDRD or externally funded limited term • Project is on approved science priority list with specific actions to address • Project is on science priority list for out year consideration • Project is not on science priority list or not considered |  |  |  | • Once a week • Once a month • Once a quarter • Once a year • Once every 2 years or longer | • One year or more • 3 months to one year • 1 to 3 months • 1 week to 1 month • 1 day to 1 week
Scoring Rules for each Criterion: | [10 empty] | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three are true, score 9 | If none are true score 0; if one is true, score 3; if two are true, score 6; if three or more are true, score 9 | If not on list score 0; if out year consideration score 3; if planning stage score 6; if current year execution score 9 |  |  |  | If once a week, score 5; if once a month score 4; if once a quarter score 3; if once a year score 2; if once every 2 years or longer, or no likely downtime score 1. | If one year or more score 5; if 3 months to 1 year score 4; if 1 to 3 months score 3; if 1 week to 1 month score 2; if 1 day to 1 week score 1
Guidance: | [10 empty] | Evaluate whether the project directly affects the ability of the facility to meet the four scope elements listed above and score accordingly. | Evaluate whether the project will affect operating power capability according to the criteria and score accordingly. | Evaluate the project to determine whether it enhances capability of more than one instrument, or the accelerator, or is a funded external project and score accordingly. | Determine whether the project must be done in response to one or more external drivers, and score accordingly. | Determine the status of the project on the current approved instrument upgrade plan and score accordingly. |  |  |  | Perform a qualitative assessment of the frequency of system-related downtime events if the project is not performed. | Perform a qualitative assessment of the duration of the downtime for each occurrence if the project is not performed
Weighting Factor: | [10 empty] | 4 | 3 | 2 | 2 | 8 |  |  |  | 1 | 1
Project Identifier | Management Status | Project | Commitment (PEMP or Business Plan) | Owning Division | Owning Group | Project Lead | Project Type | Status | Schedule | Category | Performance against published schedule | Operating power | Capability | External Drivers | Science, LDRD and External Funding Projects | Weighted Score (Criteria 1-4) | Science Score (Criterion 5) | Total Score (Criteria 1-5) | Probability (1-5) | Consequence (1-5) | Risk (1-25) | Overall Impact | Notes
APBIIS-02 | Authorized | 6D phase space grant | Yes | RAD | APBIIS | Cousineau | MIE | Active | Level of Effort | Research and Development | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY2017 Business Plan Objective 3.c. Need mechanical and electrical support | 1
APBIIS-05 | Authorized | External antenna ion source development | No | RAD | APBIIS | Welton | OIP | Active | Unscheduled | Research and Development | 9 | 3 | 3 | 0 | 0 | 51 | 0 | 51 | 1 | 1 | 1 | 5.1 |  | 2
APBIIS-06 | Authorized | AIP-37 Beam Instrumentation Infrastructure Improvements | No | RAD | APBIIS | Aleksandrov | OIP | Pending Funding | Level of Effort | Obsolescence | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 4 | 8 | 9.6 | Linac BPM upgrade, Ring BPM upgrade, BLM upgrade | 3
APBIIS-08 | Authorized | MEBT laser detector replacement | No | RAD | APBIIS | Aleksandrov | OIP | Active | Unscheduled | Low Cost Improvement | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 1.8 | Needs vacuum support for a few hours | 4
APBIIS-10 | Authorized | Electron scanner high voltage power supply replacement | No | RAD | APBIIS | Aleksandrov | OIP | Active | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7 | Electrical group is developing new power supply | 5
APBIIS-11 | Authorized | RTBT harp electronics | No | RAD | APBIIS | Aleksandrov | OIP | Pending Planning | Unscheduled | Obsolescence | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 2 | 4 | 8 | 21.6 | Upgrade and spare for existing electronics | 6
APBIIS-12 | Authorized | Injection foil video improvement | No | RAD | APBIIS | Aleksandrov | OIP | Active | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 3 | 1 | 3 | 8.1 | Need mechanical designer support | 7
APBIIS-13 | Authorized | Ring electron scanner aperture increase | No | RAD | APBIIS | Aleksandrov | OIP | Pending Funding | Unscheduled | Low Cost Improvement | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 1.8 | Need mechanical designer support | 8
APBIIS-14 | Authorized | Moderator development LDRD | No | RAD | APBIIS | Galambos | OIP | Pending Funding | Unscheduled | Research and Development | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | Need mechanical and electrical support
APBIIS-15 | Authorized | FODO Line for BTF | No | RAD | APBIIS | Aleksandrov | OIP | Active | Unscheduled | Research and Development | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | Need mechanical designer support
CON-01 | Authorized | AIP-39 Machine Protection System Improvements | Yes | RAD | CON | White | AIP | Active | Level of Effort | Obsolescence | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 3 | 3 | 9 | 56.7 | FY2017 Business Plan Objective 3.c. In design, implementation will require AIP fuding, schedule changed to Level of Effort
CON-03 | Approved | Install high power shutters DTL1/2 waveguide | No | RAD | CON | White | OIP | Active | 2017B (May-June) | Efficiency | 9 | 3 | 3 | 3 | 0 | 57 | 0 | 57 | 3 | 1 | 3 | 17.1
CON-04 | Authorized | ReplacePLCs/Panelview for Target | No | RAD | CON | Strong | OIP | Pending Resources | Unscheduled | Obsolescence | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 1 | 1 | 4.5 | This is really maintenance therefore I propose we remove it from this list.
CON-07 | Authorized | Replacement for PSC | No | RAD | CON | Curry | OIP | Pending Resources | Unscheduled | Obsolescence | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 2 | 1 | 2 | 6.6
CON-08 | Approved | Isolate FE PPS Cabinets | No | RAD | CON | Mahoney | OIP | Active | 2017B (May-June) | Efficiency | 9 | 3 | 0 | 9 | 0 | 63 | 0 | 63 | 1 | 3 | 3 | 18.9
CON-09 | Not Authorized | VENUS PPS Installation | No | RAD | CON | Mahoney | MIE | Pending Funding | Unscheduled | Efficiency | 0 | 0 | 3 | 3 | 6 | 12 | 48 | 60 | 1 | 1 | 1 | 6
CON-10 | Approved | Timing Master Installation | No | RAD | CON | Curry | OIP | Active | 2017B (May-June) | Obsolescence | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 1 | 2 | 2 | 7.2
EERF-01A | Approved | AIP-34 HVCM Controller Upgrade | Yes | RAD | EERF | Champion | AIP | Active | 2017A (January) | Obsolescence | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 3 | 1 | 3 | 19.8 | FY2017 Business Plan Objectives 2.c.2 and 3.c.
EERF-01B | Approved | AIP-34 HVCM Controller Upgrade | Yes | RAD | EERF | Champion | AIP | Active | 2017B (May-June) | Obsolescence | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 3 | 1 | 3 | 19.8 | FY2017 Business Plan Objectives 2.c.2 and 3.c.
EERF-02 | Authorized | HVCM Alternate Topology Modulator development | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Low Cost Improvement | 6 | 6 | 6 | 0 | 0 | 54 | 0 | 54 | 1 | 1 | 1 | 5.4
EERF-03 | Authorized | JEMA Modulator testing | No | RAD | EERF | Champion | OIP | Active | Level of Effort | Supply Chain | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 1 | 1 | 2.1 | CRADA with ESS-Bilbao.
EERF-04 | Authorized | Develop thryatron replacement for extraction kicker PFNs | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Low Cost Improvement | 3 | 6 | 6 | 0 | 0 | 42 | 0 | 42 | 1 | 1 | 1 | 4.2
EERF-05 | Authorized | Comprehensive update of the HVCM design drawings including red line capture | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Supply Chain | 3 | 3 | 6 | 0 | 0 | 33 | 0 | 33 | 1 | 1 | 1 | 3.3 | Essential for PPU and MaRIE and documentation of corporate knowledge.
EERF-06 | Authorized | Development of new High-Power Protection Module | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Obsolescence | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7
EERF-07 | Authorized | Development of new LLRF system | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Low Cost Improvement | 3 | 6 | 3 | 0 | 0 | 36 | 0 | 36 | 1 | 1 | 1 | 3.6 | Essential for PPU.
EERF-08 | Authorized | Improve cooling of equipment racks in klystron gallery | No | RAD | EERF | Champion | OIP | Pending Planning | Unscheduled | Low Cost Improvement | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 1 | 2 | 7.2 | McLaughlin has a proposal.
EERF-09 | Approved | Procure spare DTL circulators | No | RAD | EERF | Champion | OIP | Active | 2017B (May-June) | Spare | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 5 | 10 | 36 | Install first article during 2017B.
EERF-10 | Authorized | Procure spare klystrons | No | RAD | EERF | Champion | OIP | Pending Funding | Level of Effort | Spare | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 5 | 5 | 22.5
EERF-11 | Authorized | Develop alternative supply chain for 2.5 and 5.0 MW klystrons | No | RAD | EERF | Champion | OIP | Pending Funding | Unscheduled | Supply Chain | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 1 | 5 | 5 | 22.5
EERF-12 | Authorized | Installation of new RFQ at Front-End building | Yes | RAD | EERF | Champion | OIP | Active | 2017B (May-June) | Low Cost Improvement | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 2 | 4 | 8 | 52.8 | FY2017 Business Plan Objective 2.c.2.
EERF-13 | Authorized | Investigate and correct high-power performance of Thales 550 kW klystrons | No | RAD | EERF | Champion | OIP | Pending Resources | Level of Effort | Spare | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 2.4 | Adds ~12 klystrons to spares inventory.
EERF-14 | Approved | Develop alternative RF-Vacuum window source for DTL and CCL | No | RAD | EERF | Champion | OIP | Active | Level of Effort | Spare | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 2 | 4 | 8 | 33.6 | Continuation of work with Mega Inc. - Initial article to be installed during 2017A.
EERF-15 | Authorized | Development of the HVCM laminate buss | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7
EERF-16 | Authorized | Develop alternative source of HVCM boost capacitors | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Supply Chain | 6 | 6 | 3 | 3 | 0 | 54 | 0 | 54 | 2 | 1 | 2 | 10.8
EERF-17 | Authorized | HVCM IGBT replacement | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Obsolescence | 9 | 6 | 3 | 0 | 0 | 60 | 0 | 60 | 4 | 1 | 4 | 24
EERF-18 | Not Authorized | AIP-46 Linac Quad power supply standardization | No | RAD | EERF | Champion | AIP | Pending Funding | Unscheduled | Low Cost Improvement | 9 | 0 | 0 | 0 | 0 | 36 | 0 | 36 | 2 | 1 | 2 | 7.2
EERF-19 | Authorized | PSI upgrade | No | RAD | EERF | Champion | OIP | Pending Planning | Unscheduled | Obsolescence | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 3 | 1 | 3 | 9.9
EERF-20 | Approved | LEBT smart chopping | Yes | RAD | EERF | Champion | OIP | Active | 2017B (May-June) | Low Cost Improvement | 6 | 6 | 6 | 0 | 0 | 54 | 0 | 54 | 1 | 1 | 1 | 5.4 | FY2017 Business Plan Objective 2.c.2.
EERF-21 | Authorized | Procure spare substation transformers | No | RAD | EERF | Champion | OIP | Pending Funding | Unscheduled | Spare | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 2 | 1 | 2 | 4.8
EERF-22 | Authorized | Replace RNSS-2 switch with a remotely operated switch | No | RAD | EERF | Champion | OIP | Pending Funding | Unscheduled | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 1 | 1 | 1 | 1.2
EERF-25 | Authorized | Completion of 4-way waveguide high power distribution system | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Low Cost Improvement | 0 | 0 | 3 | 0 | 0 | 6 | 0 | 6 | 1 | 1 | 1 | 0.6
EERF-26 | Authorized | Redesign HVCM filter to minimize ripple | No | RAD | EERF | Champion | OIP | Pending Resources | Unscheduled | Low Cost Improvement | 3 | 3 | 3 | 0 | 0 | 27 | 0 | 27 | 1 | 1 | 1 | 2.7
EERF-27 | Authorized | Install UPS for Front-End vacuum controls | No | RAD | EERF | Champion | OIP | Pending Funding | Unscheduled | Low Cost Improvement | 9 | 0 | 0 | 3 | 0 | 42 | 0 | 42 | 2 | 1 | 2 | 8.4
EERF-28 | Approved | CCL RF Window Temperature Measurement | No | RAD | EERF | Champion | OIP | Active | 2017B (May-June) | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 1 | 1 | 1 | 1.2
EERF-29 | Authorized | Development of new SCL transmitter main control PCB | No | RAD | EERF | Champion | OIP | Pending Resources | Unscheduled | Obsolescence | 3 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 1 | 1 | 1 | 1.8 | Involves controls support. New PCB will be used as a spare for PSS-Main PCB. Tentative prototype delivery of Spring 2017.
EERF-30 | Authorized | SCL Transmitter Test Rack System | No | RAD | EERF | Champion | OIP | Pending Resources | Unscheduled | Low Cost Improvement | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 2.4 | Off-line test system for SCL Transmitter components and chassis.
EERF-31 | Authorized | DTL Iris coupler test cavity | No | RAD | EERF | Champion | OIP | Active | Unscheduled | Spare | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 1 | 1 | 2.1 | Required for PPU
EERF-32 | Authorized | Installation of old RFQ at BTF | Yes | RAD | EERF | Champion | OIP | Active | Level of Effort | Low Cost Improvement | 9 | 6 | 3 | 3 | 0 | 66 | 0 | 66 | 2 | 4 | 8 | 52.8 | FY2017 Business Plan Objective 2.c.2.
IDAC-03 | Approved | MANDI DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Active | 2017A (January) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 33.6
IDAC-04 | Approved | ARCS DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Pending Planning | 2017B (May-June) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 33.6
IDAC-05 | Approved | CNCS DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Pending Planning | 2017B (May-June) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 33.6
IDAC-06 | Approved | EQ-SANS DAQ/Controls Upgrade | No | RAD | IDAC | Hartman | OIP | Pending Planning | 2017B (May-June) | Obsolescence | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 4 | 1 | 4 | 33.6
INS-01 | Approved | NOMAD background reduction | Yes | CEMD | ADVDIFF | Tucker | Instrument Upgrade | Active | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-02 | Authorized | NOMAD sample changer | Yes | ISD | SNSINST | Everett | Instrument Upgrade | Active | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-03 | Approved | Magnetism Reflectometer Improvement Project | Yes | QCMD | TFN | Fitzsimmons | Instrument Upgrade | Active | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-04 | Approved | EQ-SANS Detector Vessel/Sample Area Modifications | Yes | BSMD | SDSM | Heller | Instrument Upgrade | Active | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-05 | Approved | POWGEN Phase I Upgrade | Yes | CEMD | CHEMCRYS | Huq | Instrument Upgrade | Active | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY2017 Business Plan Objective 2.d.3.
INS-06 | Approved | TOPAZ Goniometer | Yes | CEMD | CHEMCRYS | Huq | Instrument Upgrade | Active | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-07 | Approved | SEQUOIA Vacuum Upgrade | Yes | ISD | MSO | Jones (L) | Instrument Upgrade | Active | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY2017 Business Plan Objective 2.d.3. Duplicate with MSO-11 so retained this and eliminated MSO-11. Price/Stone are points of contact within MSO for this project.
INS-08 | Approved | NSE Magnetism Capability | Yes | ISD | TOF | Ehlers | Instrument Upgrade | Active | 2017B (May-June) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-09 | Authorized | 14T Magnet for SNS | Yes | ISD | SE | Stone | Instrument Upgrade | Active | 2017C (October) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-10 | Authorized | SNAP detector rebuild | Yes | ISD | ADVDIFF | Tulk | Instrument Upgrade | Pending Planning | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-12 | Authorized | VULCAN detector build-out | Yes | ISD | ENGMAT | An | Instrument Upgrade | Pending Planning | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-13 | Authorized | CORELLI Thimble | Yes | ISD | SOM | Ye | Instrument Upgrade | Pending Planning | 2019A (TBD) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-14 | Authorized | CNCS collimator | Yes | ISD | TOF | Ehlers | Instrument Upgrade | Pending Planning | 2017C (October) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-15 | Authorized | HYSPEC elevator | Yes | ISD | TOF | Winn | Instrument Upgrade | Pending Planning | 2018A (December-April) | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
INS-16 | Authorized | POWGEN: phase II detectors | Yes | ISD | CHEMCRYS | Huq | Instrument Upgrade | Pending Planning | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | FY 2017 Business Plan Objective 2.d.3.
MSO-01 | Authorized | Primary Foil Changer Spare & Test Stand | No | RAD | MSO | Roseberry | OIP | Active | Level of Effort | Spare | 6 | 9 | 0 | 0 | 0 | 51 | 0 | 51 | 3 | 1 | 3 | 15.3
MSO-03 | Authorized | Water Mist System Restoration | No | RAD | MSO | Denison | OIP | Active | Unscheduled | Low Cost Improvement | 0 | 0 | 0 | 6 | 0 | 12 | 0 | 12 | 1 | 1 | 1 | 1.2
MSO-04 | Authorized | IRP Replacement | Yes | RAD | MSO | Baumgartner | OIP | Active | 2017B (May-June) | Efficiency | 9 | 0 | 6 | 3 | 0 | 54 | 0 | 54 | 2 | 5 | 10 | 54 | FY2017 Business Plan Objective 2.d.4.
MSO-05 | Authorized | HWS #4 Heavy Water Conversion | Yes | RAD | MSO | Jacobs | OIP | Active | 2017B (May-June) | Low Cost Improvement | 0 | 0 | 6 | 3 | 3 | 18 | 24 | 42 | 1 | 1 | 1 | 4.2 | FY2017 Business Plan Objective 2.d.4.
MSO-06 | Authorized | COHERENT Experiment | No | NScD | FAC | Vogel | MIE | Active | Unscheduled | Research and Development | 0 | 0 | 3 | 0 | 9 | 6 | 72 | 78 | 1 | 1 | 1 | 7.8
MSO-07 | Authorized | Helium Gas Injection | Yes | ISD | SDEA | Jacobs | OIP | Design | 2017B (May-June) | Low Cost Improvement | 9 | 9 | 3 | 6 | 0 | 81 | 0 | 81 | 3 | 2 | 6 | 48.6 | FY2017 Business Plan Objective 2.c.2.
MSO-08 | Authorized | Contaminated Relief Valve Test Stand | No | RAD | MSO | Denison | OIP | Pending Resources | Unscheduled | Low Cost Improvement | 0 | 0 | 0 | 3 | 0 | 6 | 0 | 6 | 1 | 1 | 1 | 0.6 | ACTS 0.31205
MSO-10 | Approved | BL17 Turbo Integration--SCHW Cooling | No | RAD | MSO | Jacobs | OIP | Active | 2017B (May-June) | Low Cost Improvement | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2
MSO-12 | Authorized | RF Window "Post-Conditioned" Vacuum System | No | RAD | MSO | Price | OIP | Pending Funding | Unscheduled | Low Cost Improvement | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 2 | 2 | 4 | 12
MSO-13 | Authorized | Servo-Manipulator Replacement | No | RAD | MSO | Denison | AIP | Pending Planning | Unscheduled | Obsolescence | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 1 | 1 | 1 | 3
MSO-14 | Approved | AIP-35 Warm Linac Vacuum Upgrade | Yes | RAD | MSO | Stone | AIP | Active | 2017A (January) | Obsolescence | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 5 | 1 | 5 | 21 | FY2017 Business Plan Objective 3.c.
MSO-15 | Authorized | AIP-36 HVCM Cooling Upgrade | Yes | RAD | MSO | Schubert | AIP | Pending Funding | Unscheduled | Low Cost Improvement | 9 | 9 | 0 | 0 | 0 | 63 | 0 | 63 | 3 | 1 | 3 | 18.9 | FY2017 Business Plan Objective 3.c.
MSO-16 | Approved | Heavy Water Receipt and Sampling | Yes | RAD | MSO | Jacobs | OIP | Active | 2016C (October) | Low Cost Improvement | 0 | 0 | 6 | 3 | 3 | 18 | 24 | 42 | 1 | 1 | 1 | 4.2 | FY 2017 Business Plan Objective 2.d.4. Will begin before 2016C, and conclude after end of 2016C.
MSO-17 | Authorized | LINAC Plug Door Replacement | No | RAD | MSO | Roseberry | OIP | Active | Unscheduled | Safety | 0 | 0 | 0 | 3 | 0 | 6 | 0 | 6 | 1 | 1 | 1 | 0.6
MSO-18 | Authorized | Chicane 02 Vacuum Vessel and e-catcher emergency Spare | No | RAD | MSO | Roseberry | OIP | Active | Level of Effort | Spare | 6 | 6 | 0 | 0 | 0 | 42 | 0 | 42 | 1 | 4 | 4 | 16.8
MSO-19 | Authorized | Chicane 02 Vacuum Vessel Upgrade | No | RAD | MSO | Roseberry | OIP | Pending Planning | Unscheduled | Low Cost Improvement | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 1 | 4 | 4 | 13.2 | Incorporates prior duplicate tasks APBIIS-03 (Moved to Completed Projects) and MSO-02 (Eliminated). Roseberry has lead to coordinate with Plum.
MSO-20 | Authorized | Next Generation Primary Foil Changer Mechanism | No | RAD | MSO | Roseberry | OIP | Pending Planning | Unscheduled | Low Cost Improvement | 0 | 6 | 3 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 2.4
MSO-21 | Authorized | Next Generation Secondary Foil Changer Mechanism | No | RAD | MSO | Roseberry | OIP | Pending Planning | Unscheduled | Low Cost Improvement | 0 | 6 | 3 | 0 | 0 | 24 | 0 | 24 | 1 | 1 | 1 | 2.4
MSO-22 | Authorized | DTL Spares Initiative | No | RAD | MSO | Roseberry | OIP | Pending Funding | Unscheduled | Spare | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 1 | 4 | 4 | 4.8
MSO-23 | Authorized | LEDP UPGRADE | No | RAD | MSO | Roseberry | OIP | Pending Planning | Unscheduled | Low Cost Improvement | 0 | 3 | 0 | 0 | 0 | 9 | 0 | 9 | 1 | 1 | 1 | 0.9
MSO-24 | Authorized | Separate Front End DI Water Loop from KL-04 DI Water Systems | No | RAD | MSO | Norman | OIP | Pending Planning | Unscheduled | Low Cost Improvement | 6 | 9 | 0 | 0 | 0 | 51 | 0 | 51 | 2 | 1 | 2 | 10.2
MSO-25 | Authorized | Remote auto fill of Collimators cooling skids | No | RAD | MSO | Smith, C. Craig | OIP | Pending Funding | Unscheduled | Low Cost Improvement | 6 | 9 | 0 | 0 | 0 | 51 | 0 | 51 | 2 | 1 | 2 | 10.2
MSO-26 | Authorized | Accelerator System CAD Model | No | RAD | MSO | Roseberry | OIP | Pending Funding | Unscheduled | Low Cost Improvement | 0 | 3 | 3 | 3 | 0 | 21 | 0 | 21 | 1 | 4 | 4 | 8.4
MSO-28 | Not Authorized | Replace All Shutter Lifting Rods | No | RAD | MSO | Denison | OIP | Pending Funding | Unscheduled | Low Cost Improvement | 3 | 0 | 3 | 6 | 0 | 30 | 0 | 30 | 1 | 1 | 1 | 3
MSO-30 | Approved | Replace Obsolete MKS Gauge Controllers | No | RAD | MSO | Price | OIP | Active | 2017B (May-June) | Obsolescence | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 3 | 1 | 3 | 7.2
MSO-31 | Approved | Replace RTBT T-SectionTurbos / Controllers | No | RAD | MSO | Price | OIP | Pending Resources | 2017B (May-June) | Low Cost Improvement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0
MSO-32 | Approved | Reconfigure LEBT Foreline Valves and Controls | No | RAD | MSO | Price | OIP | Active | 2017A (January) | Low Cost Improvement | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 2 | 1 | 2 | 4.8
MSO-33 | Authorized | Add Temperature Measurement to Warm Linac SGVs | No | RAD | MSO | Price | OIP | Pending Resources | Unscheduled | Low Cost Improvement | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 1 | 2 | 2.4
MSO-34 | Authorized | NexGen Ion Pump Controller Evaluation | No | RAD | MSO | Price | OIP | Pending Resources | Unscheduled | Supply Chain | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 3 | 1 | 3 | 7.2
PPU-STS | Approved | Proton Power Upgrade - Second Target Station | Yes | PPU-STS | PPU-STS | Galambos | Facility Upgrade | Active | Level of Effort | Facility Upgrade | 0 | 9 | 9 | 9 | 9 | 63 | 72 | 135 | 1 | 1 | 1 | 13.5 | FY2017 Business Plan Objective 2.e.a. Need mechanical and electrical support
SCLS-01 | Authorized | Medium Beta Spare Cryomodule | No | RAD | SCLS | Kim | OIP | Pending Funding | Level of Effort | Spare | 9 | 9 | 0 | 3 | 0 | 69 | 0 | 69 | 2 | 2 | 4 | 27.6
SCLS-02 | Approved | Plasma Hardware for Multiple Cryomodule Deployment | Yes | RAD | SCLS | Kim | OIP | Active | 2017B (May-June) | Efficiency | 3 | 9 | 3 | 6 | 0 | 57 | 0 | 57 | 1 | 1 | 1 | 5.7 | FY2017 Business Plan Objective 2.c.2. Required to support SCLS-05 during 2017B.
SCLS-03 | Authorized | Spare Carbon Bed | No | RAD | SCLS | Kim | OIP | Active | Level of Effort | Spare | 9 | 0 | 0 | 6 | 0 | 48 | 0 | 48 | 1 | 4 | 4 | 19.2 | Bids covering the installation received 7/15/16 and are being evaluated.
SCLS-04 | Not Authorized | AIP-44 SCL Cavity Chemistry Facility | No | RAD | SCLS | Kim | GPP | Pending Funding | Unscheduled | Capability | 3 | 3 | 3 | 3 | 0 | 33 | 0 | 33 | 1 | 1 | 1 | 3.3
SCLS-05 | Approved | Plasma processing in the tunnel | Yes | RAD | SCLS | Kim | OIP | Active | 2017B (May-June) | Low Cost Improvement | 3 | 9 | 3 | 6 | 3 | 57 | 24 | 81 | 1 | 1 | 1 | 8.1 | FY2017 Business Plan Objective 2.c.2. Goal is to apply plasma processing to 5 high beta cryomodules during the long shutdown for IRP change using hardware from SCLS-02.
SCLS-06 | Not Authorized | SCLS vacuum improvement | No | RAD | SCLS | Kim | AIP | Pending Planning | Unscheduled | Low Cost Improvement | 9 | 3 | 0 | 3 | 0 | 51 | 0 | 51 | 4 | 1 | 4 | 20.4 | Add isolation valve and small turbo pump at the cryomodule pump-drop. Install roughing pump line for the turbos. Improve insulating vacuum system.
SCLS-07 | Authorized | Engineering and hardware development for CHL 2K cold box repair | No | RAD | SCLS | Kim | AIP | Pending Planning | Unscheduled | Supply Chain | 6 | 0 | 0 | 3 | 0 | 30 | 0 | 30 | 1 | 4 | 4 | 12
SCLS-08 | Authorized | Engineering and hardware development to keep SCL cold at around 80 K during long CHL shutdown | No | RAD | SCLS | Kim | AIP | Pending Planning | Unscheduled | Efficiency | 3 | 0 | 0 | 3 | 0 | 18 | 0 | 18 | 1 | 5 | 5 | 9
SCLS-09 | Authorized | VFD test stand for cold compressor | No | RAD | SCLS | Kim | OIP | Pending Planning | Unscheduled | Efficiency | 6 | 3 | 0 | 0 | 0 | 33 | 0 | 33 | 2 | 1 | 2 | 6.6
SCLS-10 | Approved | CM9, CM19 insulating vacuum backflow preventer improv. | No | RAD | SCLS | Kim | OIP | Active | 2016C (October) | Low Cost Improvement | 9 | 3 | 0 | 0 | 0 | 45 | 0 | 45 | 2 | 3 | 6 | 27 | Some Controls work remaining
SSG-01 | Not Authorized | RAD Shop & Assembly Building | No | NScD | SITE | McLaughlin | GPP | Pending Funding | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 9 | 0 | 72 | 72 | 1 | 1 | 1 | 7.2 | Conceptual effort needed to establish site and funding needs
SSG-02 | Authorized | Klystron Gallery HVAC System Improvements | No | RAD | SITE | McLaughlin | OIP | Pending Funding | Unscheduled | Efficiency | 3 | 0 | 0 | 3 | 0 | 18 | 0 | 18 | 2 | 1 | 2 | 3.6 | On-going issue with air circulation for cooling the instrument racks. Needs support from CUB (chilled water) and Controls Group.
SSG-03 | Authorized | Klystron Gallery Outside Lighting Rework | No | NScD | SITE | McLaughlin | OIP | Pending Funding | Unscheduled | Efficiency | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 2 | 1 | 2 | 2.4 | DCN RAD-8300-078 complete which retrofits the existing Klystron Gallery wall mounted lighting fixtures with 35 watt, 277v LED Lamps. Retrofit the west end street lights with direct replacement 110 watt, 480V LED lighting heads. Provide an isolation transformer feeding a new emergency lighting panel to re-feed the above mentioned lighting fixtures in items 1 &2 to prevent ground faults from migrating back to the unit substation.
SSG-04 | Approved | Target Building - AHU #9 Needs Re-balanced and re-commissioned and the Controls Upgraded | No | NScD | SITE | McLaughlin | OIP | Active | 2017A (January) | Efficiency | 0 | 0 | 3 | 0 | 0 | 6 | 0 | 6 | 2 | 1 | 2 | 1.2 | Supports COHERENT LDRD Project as well as the current system not performing as designed. Controls Group preparing the DCN. Systematic TAB performed TAB on July 21 and 22nd. Report issued August 2, 2016.
SSG-05 | Not Authorized | CRMB Mezzanine Addition | No | RAD | EERF | Champion | OIP | Pending Funding | Unscheduled | Facility Upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | Desire to better utilize the high bay space on the ground floor.
SSG-06 | Authorized | Tie-in and Valving for Second Elevated Water Storage Tank | No | DOO | SITE | McLaughlin | Facility Upgrade | Pending Planning | 2017B (May-June) | Capability | 0 | 0 | 0 | 6 | 9 | 12 | 72 | 84 | 1 | 1 | 1 | 8.4 | Summer outage provides an opportunity to execute this work with minimal impact on operations.