## Slide 1: SNS 2017 AAC Outbrief
Rod Gerig Chair
March 10, 2017

## Slide 2: Topic: Operations
Since the last meeting the SNS team has achieved sustained operations with beam powers between 1.0 and 1.2 MW.
In FY16 5,832 operating hours were achieved (exceeding the neutron production target of 5,000 hours), with 4,230 hours delivered to the user community. Availability was 92.9%, excluding two target failures (T12 & T13), but 86.4% including them. Target failures accounted for 47% of downtime in FY16.
FY17 started with excellent machine performance, but mitigating the recent Inner Reflector Plug leak has resulted in some unplanned downtime.
Excluding target failures >90% availability is now regarded as routine, to the extent that the DOE is becoming less interested in this as a key performance indicator (being more interested in hours delivered). However, there is evidence from other neutron sources that availability is actually one of the most important factors in the user experience at a facility.

## Slide 3: Topic: Operations (continued)
Performance metrics and downtime analysis at SNS are particularly strong, and clearly show that the team has achieved year-on-year reductions in <1 minute downtimes.
Long downtime events continue to have an impact on scheduling, performance, and beam power levels.
Continue to put the user experience at the facility at the forefront of thinking on availability, beam power levels and scheduling.

## Slide 4: Topic: Ion Source, RFQ and BTF
Beam Test Facility
The buildup of the beam test facility (BTF) has progressed greatly and is a significant improvement to operations and beam physics.
A first pass at possible subjects were displayed. It should be managed so that these planned and future experiments do not interfere with the laboratories primary mission. Source development, LEBT-RFQ gate valve, chopper target and upgraded emittance scanner and associated hardware should continue and be prioritized by supporting it with both labor and funds.
Continued development of the external RF antenna is a good idea and could eventually provide either longer lifetime sources and/or alleviate antenna vendor concerns.

## Slide 5: Topic: Ion Source, RFQ and BTF
Ion Source
This past year (FY16) has been very productive for both ion source development and operations.
The ion source operations registered about 32 hours of downtime out of the approximately 5500 hours of operations. The source has taken advantage of target and other outages to replace sources as to not incur downtime.
The present RF internal antenna design has made progress in understanding lifetime issues and believe with present antenna coating thickness will continue to fit into planned target changes. An issue with cooling lines and breakdown was identified and corrected largely by extending the length and the use of clear tubing to allow visual inspections.
ISTS remains a critical part of operational reliability and should not be forgotten with the buildup of another test facility.

## Slide 6: Topic: Ion Source, RFQ and BTF
RFQ
The committee congratulates SNS for the successful testing of the new RFQ! The BTF has allowed the testing of the new RFQ at desired power and has verified its capability to deliver the desired beam parameters. The success of this work can’t be emphasized enough and should allow SNS to move forward with the eventual swap of RFQs.
The RFQ as configured in the BTF has demonstrated the requirements needed for PPU.
Consider ordering an RFQ spare that would meet facility requirements.

## Slide 7: Topic: Superconducting Linac / SRF
It is encouraging that the reliability and availability of the superconducting linac has generally been good for the past 6 years. The SNS team reports that some degradation of cavity performance is observed over time, but that it can be recovered during outage periods. The committee commends the SNS team on the success of their ‘Superconducting Linac Stewardship Program”.
The committee was happy to hear about significant progress on the preparation of a spare medium-beta cryomodule, following a methodology similar to the successful fabrication of the spare high-beta cryomodule. We view these efforts as being important to the SNS mission. Completion of the spare medium-beta cryomodule before the ramp-up of PPU activities would be beneficial for both the SNS mission and PPU. The plan to add a spare carbon bed for purification of helium gas returned to the CHL project is also viewed by the committee as being a good investment in sustainability.

## Slide 8: Topic: Superconducting Linac / SRF
The SNS team has made a significant investment in SRF infrastructure over the past several years. Recent R & D activities have been oriented toward better-quantifying preparation steps and cleanliness. The committee views this R & D work as being worthwhile for the existing SNS scope as well as future upgrades.
So far no funding has been made available for in-house etching or electropolishing. This necessitates outside partners for cavity R & D and cryomodule development. The SNS team might consider allocating some funding to developing some minimal capabilities for chemical etching and planning for a future larger-scale facility.
Seven additional high-beta cryomodules are needed for PPU. The plan is to outsource the fabrication of these cryomodules to a partner lab. This plan is similar to the approach used to build the existing linac.

## Slide 9: Topic: Superconducting Linac / SRF
Plasma Processing of SRF Cavities
Three high-beta cryomodules have been plasma-processed, two of which are operating in the linac. This has allowed for an increase in the linac energy from 939 MeV to 972 MeV; a reduction in X-ray production has been observed after plasma processing. The committee congratulates the SNS team on these excellent results.
Additional plasma processing in the SNS tunnel is planned for future outages, and the target cryomodules have been selected. A second plasma processing station will be used to allow for processing of two cavities in parallel. The committee views this as a good investment.
A variable coupler has been developed for use in Dewar tests. It is anticipated that this will allow for measurements of the intrinsic quality factor after plasma processing. The committee sees this as being a worthwhile endeavor which will be of interest to the SRF community.

## Slide 10: Topic: Superconducting Linac / SRF
A partnership has been initiated with 2 other labs to study plasma processing of cavities of a different design and with different surface preparation. The committee sees this as a positive development which may ultimately benefit the accelerator community
SCL Recommendations:
Proceed with the fabrication of the spare medium-beta cryomodule; if possible, make sure the funding profile is adequate to complete this task in a timely manner
Continue to emphasize the SRF R&D program at SNS, particularly to support PPU.

## Slide 11: Topic: Ring (includes foils, laser stripping, AP, e.g., self consistent beams)
The present Electron catcher for convoy electrons from the ring injection stripper is not properly aligned and does not absorb all of convoy electrons, thus many are accelerated back to the foil holder and have cause thermal damage to the foil holder. A new removable catcher is being designed and is a priority for 1.4 MW operations. This has been included in the prioritization process, and addresses a recommendation from the last meeting.
Stripper foil development is a significant ongoing development effort especially for the PPU and STS projects. At 1.3 GeV the stripper foil thickness needs to increase 8% and the energy deposited in the foil will be ~50% higher than at 1.0 GeV, thus significantly raising the foil temperature and reducing foil lifetime by an unknown factor. This is a critical area that requires ongoing attention.

## Slide 12: Topic: Ring (includes foils, laser stripping, AP, e.g., self consistent beams)
Laser stripping is a promising long range basic research effort carried out by post docs and graduate students. It is making significant progress of great value to the larger Accelerator community and should continue to be supported.
The committee heard very promising progress on the renewed computational efforts on the development of “Self-Consistent Beam Distributions” along with possible hardware modifications to the SNS ring to create a self-consistent beam distribution. The next steps would be valuable checks on the feasibility of these changes and more study of the modeling especially of fringe field effects.

## Slide 13: Topic: Target Systems - IRP
Currently installed IRP is approaching to the end of life and developed water leak. The water leak was large and required rerouting back into the closed loop. The exact location of the leak is not known. SNS should be concerned about moisture within the core vessel and IRP. Circulation of helium gas is a potential mitigation.
The original IRP-01 should be replaced as soon as IRP-02 becomes available. The production schedule for the IRP-02 has been longer than 8 years. During the final stages of fabrication, the IRP-02 developed a leak, requiring repair. The IRP-02 is scheduled to arrive August 2017 with substantial effort from SNS target team working directly with the vendor. Schedule slippage could affect outage schedule.
Next-generation IRP-03 will incorporate lessons learned – changes appear well conceived (laser welding and additive manufacturing could be further options). The robustness and lifetime of the IRP should be reconsidered as the SNS beam power increases. Future IRP construction plans not developed; question of spare and strategy.
Option of power reduction in present IRP to extend lifetime. Continued communication with beamline scientist, especially if delay becomes likely

## Slide 14: Topic: Target Systems - IRP
IRP form factor could be improved for disposal, potential modularity. The lifetime could be extended through improved moderators and structural materials.
Recommendations:
Consider PIE of IRP-01 to clarify root cause of the water leak for IRP-03 design.
Work with the vendor to deliver the IRP-02 per current schedule (August 2017) by providing support in engineering, welding, inspection, and leak testing. Actively anticipate any production delays in order to inform scheduling, in case a delay of installation is required.
Consider off-line cryogenic testing of the IRP-02 prior the installation in December 2017.
Consider measures to increase the lifetime of future IRPs.

## Slide 15: Topic: Target Systems - Operations
Target 13 leaked - ran to 2600 MW-hr-, was the second target to run for a long time near 1.4MW; cavitation damage similar to T12 leak. Target 14 completed its run: 1.0MW for 2700MW-hr. Target 15 completed its run, but was preemptively removed for concern about potential damage based on T14 PIE. Target 16 has just begun. -1.2MW for 1700MW-hr.
16 targets have been operated: 7 have leaked mercury. Current operational target is a jet-flow. Improvements to the design are inevitable, given time to incorporate these solutions. Changes in mercury flow path to reduce cavitation damage. Optimization of the structure to resist cyclic loads. Mixing inert gas into the flowing mercury to reduce structural loading and cavitation damage.
Jet flow is a promising method, but unclear if it mitigates corner leakage. Numerical simulation continues to be needed so as to understand and improve the design. Engineering judgment is extensively used in concert with simulations. Furthermore, erosion model is known to be incomplete and requires further development and input from PIE.

## Slide 16: Topic: Target Systems - Operations
Interactions between fatigue and cavitation damage imply development of mitigation technique on pressure waves, thermal stress is essential.
Target carriage issue: seriously consider repair or replacement: make yearly plan to address issues
Mercury process system has several issues that have been identified, which may be exacerbated by gas injection. Replacement and coordination should be considered
Recommendations:
None

## Slide 17: Topic: Target Systems - Target Management Plan
In the target manage plan the PIE supplies the key information. Add the timing on the schedule to make decisions for the next steps. The Target Management Plan the only way to obtain realistic damage information and the greatest promise for future design improvements.
The eventual goals of 1.4 MW, two target changes per year, and no unplanned target changes are appropriate. In the short term, building to 1.4 MW with three target changes per year will be the approach to build confidence. This approach allows implementation of improved target features and collection of PIE data, while supporting a vital user program
The balance and conflict between operation and development conditions is likely to be well considered in the target manage plan. The ongoing and planned activities which SNS is pursuing can still be expected to provide the team on future development needs in preparation for higher power (1.4 MW and above) on a useful time scale.

## Slide 18: Topic: Target Systems - Target Management Plan
However, some uncertainty in the plan’s execution does remain. The mechanism of mitigation by jet flow is not clear. The erosion at corner may not be sufficiently mitigated by only the jet flow. In parallel, the numerical simulations should continue. Margin preserved for irradiation degradation and Liquid Metal Embrittlement (LME). Continue to reconsider the structural design of vessel. PIE is important throughout this process.
The Target Management Plan is a living document, signed-off by division heads. Division heads are aware that additional resources are needed to achieve the plan and have therefore committed to increasing budgets to be consistent with the plan.
2 MW target design plans are at a very preliminary level. Intent is a workable 2 MW design without gas injection, then take gas injection for additional reliability and longevity margin. Automated optimization tools were offered as a path, but they include great risk and cost as no initial estimate of performance improvement can be made and convergence can be elusive. PPU will need to develop a plan for a 2 MW target.

## Slide 19: Topic: Target Systems - Target Management Plan
Recommendations:
Management must be vigilant to support the budget needs of the target management plan as it evolves, particularly the support of ancillary activities such as PIE.
Start developing concepts for target features to allow 2 MW operation for PPU. The presented approach of “Interactive Design Space Exploration” may be valuable, but presents no specific concepts for marginal performance improvements. The data on gas injection is not sufficient at those powers, and cannot be relied on as a design feature without additional research.

## Slide 20: Topic: Target Systems – Gas Injection
Gas injection is contingent on an extensive installation in summer. Expect that an accelerator-readiness review is required because of an unreviewed safety issue determination. October startup goal requires installation in summer to allow review. Good cooperation is required with DOE site office. DOE needs a plan (and buy in) on how SNS will stage, install, review, and address all safety issues. Several uncertainties remain in the process, and demonstration remains a priority for the ultimate success of the Target Management Plan.
Potential improvements with gas flow are a substantial reduction in the stress (leading to fatigue) and void formation (leading to erosion). These have been validated at various experiments, but the correspondence is not precise.
Initial installation is only a low-flow system, but is integral to achieving 1.4 MW. Eventual high-flow implementation is conceived, but has rightly been a lower priority.
Gas bubble injection system has and will need significant effort – focus must be maintained. Improvement of analytical model to simulating mercury with bubbles is essential. Consider cooperate with J-PARC team.

## Slide 21: Topic: Target Systems – Gas Injection
Recommendations:
Maintain momentum towards deployment of the gas injection system as an integral part of the Target Management Plan.

## Slide 22: Topic: Target Systems – PIE
An 8-step post-irradiation examination procedure has been developed for each target with mandatory and optional sections.
The videoprobe inspections on failed targets are vital to maintaining a history, and should be maintained. Target sectioning has also become quite systematic for quantitative measurement of erosion (laser-scanning). Tensile tests are valuable for radiation-damaged properties of materials.
Consistent damage and cracking of central baffle has been observed, not leading to failure, but putting the target into an unmodeled condition, potentially with parts colliding into each other. The feature is a liability as the target power is increased, and should be redesigned or removed.
Feature determining cavitation damage on the target shell is the pressure wave interference pattern, dominated by the structure mechanics of the target shell. Once damage has occurred, other effects may come into play and determine damage propagation. An important feature might be the weakening of the structure by erosion and hence an increased tensile stress in the center line of the target window and the center baffle.

## Slide 23: Topic: Target Systems – PIE
Quantitative, systematic data have been quite a step forward. PIE will continue to be responsive to conditions, but consistency is also quite valuable in making use of the quantitative data.
Proton beam window removed with a water leak in the core vessel, but PIE was inadequate to find leak location. A vulnerability potentially remains.
Recommendations:
Support for PIE has been adequate, and must remain strong. PIE activities should be considered a mandatory part of the target lifecycle, and cannot be avoided or delayed indefinitely.
If possible, Perform PIE on the removed proton beam window to find the water leak location on the core vessel side.

## Slide 24: Topic: Target Systems – Hot-Cell Servomanipulators
SNS has two devices, absolutely critical for operations and PIE. The vendor is out of business. Many parts are of high concern. Use of devices has already been limited to extend lifetime.
Potential outage during replacement is 3-6 months, therefore planning and coordination is required.
Options were identified, and replacement chosen as approach (with using high-bay device as contingency). Phased plan has been explored, but there are many inputs which may affect the schedule or technical requirements. Starting Phase I – planning immediately would be prudent as risk mitigation. The phased replacement of the two devices is also prudent.
Two vendors were extensively investigated, both appeared to be adequate, and one preferred. Quantitative scoring of technical capability was used, but may be overly prescriptive and did not include issues of cost, risk, support, etc.

## Slide 25: Topic: Target Systems – Hot-Cell Servomanipulators
Cabling is a particular issue that may require a different issue, and may not be supported by vendors. It could also be performed preemptively, though with significant risk and schedule impact.
Customized machines are an optional alternative to a very general-purpose servomanipulator, but carry risks and costs related to storage and handling. While perhaps not attractive, it should not be ignored.
Recommendation:
Produce a management plan or roadmap, with decision points and inputs from operations and projects for replacement of the servomanipulators. Start proceeding with “Phase I” of project planning as soon as possible.

## Slide 26: Topic: Pulsed Power and Electrical Systems
Most of proposed improvement recommended for the HVCM has been implemented, such as the IGBT snubbers, new controller to improve the trigger control resulting in correction of the output voltage droop, and operation at full pulse width have resulted in elimination of the catastrophic IGBT failures.
The alternative topology modulator has been implemented and under test and offered improvement in operation at higher power levels. A decision on the conversion of HVCM to the new topology should be made.
Preventive maintenance replacement of high failure rate capacitors will keep the modulation reliability high until a confirmed replacement can be installed.
The use of an oil gas analyzer could detect incipient failures inside the tank before they become a serious problem requiring a long down time.
More klystron spares should be ordered, before they reach end of life

## Slide 27: Topic: Controls
Responses to 2016 recommendations were good.
  Participation in DHS Industrial Control Systems Joint Working Group is a good thing.
  System validation using ICS-Cert tools is to be commended.
  Disk to disk backup is a good enhancement.
  Testing restore from backup regularly.
  Code management for PLCs is moving forward. The commercial tool (Asset Center) being used looks powerful.
  Keep moving forward to include PPS in code management.
  CSS Display Builder approach looks promising.
Increased number of hardware failures last year (still within downtime budget). SNS may have to live with this for a while. Steps made to address obsolescence from within group’s budget are good.

## Slide 28: Topic: Controls (continued)
Hiring early career people is sensible giving age profile of group.
Achieving such diversity in hiring is commended.
Moving from OMS58 to PLC solution makes sense.
Recommendations:
Evaluation of the SLAC archiver was useful. Look for collaboration opportunities in archiving before going it alone.
Consider holding a design review for the high-performance system (currently uTCA) solution.

## Slide 29: Topic: Diagnostics
The committee was pleased to hear the report on 6D measurements, which is innovative and should continue.
It is important to measure the stripper foil temperature at present operating currents. Measurements using thermal imaging are promising and are encouraged. With this as a baseline, the changes for PPU and STS can be more reliably calculated.
Hardware and software obsolescence is a recurring theme for diagnostics as well as other systems. The diagnostics AIP-37 is scheduled to begin in FY17. Obsolescence is a growing concern and should be continually addressed in a systematic facility-wide approach.

## Slide 30: Topic: Proton Power Upgrade and Second Target Station
A pre CD-1 Director’s review of the PPU Project was recently held that determined that technically the PPU is ready to proceed.
A draft Project Assumptions Document has been written which defines the work scope that will be done by the NScD operations budget. These are items that ensure the SNS is capable of delivering beam at 2.0MW and 1.0 GeV, the design deliverables of the SNS project. Therefore this work is planned and ongoing.
A concern of the the SNS staff, and of reviewers (i.e., pre CD-1 review) is the effective matrixing of the SNS staff such that both operations and the project can effectively be done. At the last AAC meeting this committee noted that…
    “It is therefore essential that SNS develop the outage planning tools (e.g., using resource loaded scheduling during outages, and well developed prioritization) to be ready for PPU installation work.”

## Slide 31: Topic: Proton Power Upgrade and Second Target Station (continued)
We feel that SNS has made significant progress over the past year in addressing this approach. The organization has embraced this mindset. For the present work, this moving in the right direction, and this push needs to continue. Until there is actual PPU work a final assessment can not be made but the committee feels that application of these tools prior to the PPU is essential.
Recommendation:
Continue to develop and use the Project Prioritization System for all ongoing SNS work, keeping in mind the the factors that the PPU project will bring to this challenge. More on this in charge question 5.

## Slide 32: 2017 SNS AAC Charge Context
All SNS accelerator and target-related activities over the next two years are aimed at two key objectives:
By the end of FY 2018 achieve sustainable and predictable routine operation at or near 1.4 MW to the First Target Station (FTS) with availability against published schedule of ≥ 90% while using 3 target vessels per year.
Enable success of the Proton Power Upgrade project by providing key technical and management resources as required to meet project objectives.

## Slide 33: Charge Question 1: Do the capability and performance of the accelerator complex and neutron source support achieving Objective A?
The accelerator as it stands today is capable of meeting Objective A, but with very little operational margin.
Considerable progress has been made since the last meeting on the key accelerator performance improvements required to achieve a suitable beam power margin and to mitigate known vulnerabilities for high power operation. The trajectory of this work appears to be correct and well aligned with the timescale of the end of FY18.
Efforts to increase the beam power margin have concentrated on the ion source performance (increased current and extended source lifetime achieved), spare RFQ (fully tested on BTF and ready for installation), in situ plasma processing (on track for 1 GeV in 2018) and smart chopping (new infrastructure installed and waiting for test).
Vulnerabilities for operating at high power are being addressed with new in-house foil production capabilities and an electron catcher redesign in progress, but further R&D will be required to be confident of meeting the high power specification

## Slide 34: Charge Question 1: Do the capability and performance of the accelerator complex and neutron source support achieving Objective A?
Since the last meeting significant progress in target technology has been made for target design and development, including better understanding of current cavitation damage erosion limits, improved post-irradiation examination and initial implementation of gas injection.
The ‘Target Management Plan’ has been assembled to manage the risk of user program interruption while successfully handling increasing beam powers and advancing jet-flow target operation with incremental design improvements.

## Slide 35: Charge Question 1: Do the capability and performance of the accelerator complex and neutron source support achieving Objective A?
Recommendations:
Achieving Objective A will require successful replacement of the Inner Reflector Plug, as well as accelerator and target improvements, all of which must proceed in parallel during FY17 & FY18. The team should produce a resource loaded schedule for all of this work to ensure that it is feasible with the overall amount of effort available.
Achieving Objective A will also require all of the ongoing obsolescence, sustainability and AIP work to continue, and the team must ensure adequate funding and effort for this work.
Review all critical vulnerabilities for achieving Objective A, including whether spares provision for large items such as the RFQ and IRP is desirable or essential.

## Slide 36: Charge Question 2: Is the Prioritization process and Project Planning strategy that has been developed and is in use for outage planning reasonable?
Yes, a new process is in place which is more quantitative and integrates overall facility activities. This significant process includes:
  A quantitative prioritization process documented in a spreadsheet. This process has undergone several iterations and now appears to be providing consistent, reasonable priority lists, now taking such things as safety relevance into account.
  A documented “block” schedule of facility-wide activities which provides a documented framework in which teams may be able to coordinate their individual activities with site-wide constraints such as power outages.
  The Accelerator Operations Group Leader now wears a double hat as the SNS Outage Manager and professional project controls support has been engaged to further enable this process.
  A detailed outage schedule which contains information about the priority projects selected for that outage (documented via memo by the RAD Director) and has more recently been expanded to include standard maintenance activities. Refinements will continue.

## Slide 37: Charge Question 2: Is the Prioritization process and Project Planning strategy that has been developed and is in use for outage planning reasonable?
  The strategy of quantifying the project prioritization process, selecting the highest priorities for the next outage, documenting this set of priorities via memo, documenting the facility-wide schedule/constraints, and implementing and updating a detailed outage schedule with logical ties and resource loading is now in place and being refined. This appears to be a reasonable process/strategy.
Recommendation:
As SNS continues to use and refine this process, start quantitatively analyzing the available resource loading information.

## Slide 38: Charge Question 3: Is the operating strategy with three outages per year reasonable?
A ‘typical’ three outage year would have two outages of about six weeks each and one outage of about two weeks. These outages must facilitate target changes and also provide for accelerator and source maintenance and development.
This new regime will provide roughly the same number of operating hours as the current two outage year, but limits the maximum duration of maintenance periods.
There will be some reduction in flexibility for doing accelerator work, but this is considered as something which can be managed.
The three outages per year operating strategy appears appropriate for managing predicted target lifetimes and avoiding unplanned outages.
The RAD Division Director has a draft long range facility schedule to 2025 based on three outages per year which takes account of requirements for 1.4 MW operation by the end of FY2018 and the Proton Power Upgrade.

## Slide 39: Charge Question 3: Is the operating strategy with three outages per year reasonable?
Recommendation:
The team should review the effectiveness of the three outages per year operating strategy at regular intervals to ensure that it remains optimal.

## Slide 40: Charge Question 4: Is the scope of work and prioritization process for ongoing and future Accelerator Improvement Projects (AIP) appropriate and balanced between the competing interests building necessary margin for routine operation at 1.4 MW while addressing system obsolescence?
The scope of work being considered seems appropriate with both building operating margin and addressing obsolescence projects being submitted. The number of projects that can be funded via AIP causes the committee some concern.
Going forward, the need to address operating margins, obsolescence and preparing the accelerator for the PPU, the current funding level seems unsustainable. A level of funding of between $5M to $7M seems reasonable from what the committee saw.
The AIP prioritization process used appears similar to the broader process presented for project prioritization. There appears to be much merit in making these processes as similar as possible if not the same. The process appears to be fit for purpose, and should continue to be improved as experience is gained.

## Slide 41: Charge Question 5: Are non-AIP accelerator and beam delivery initiatives addressing issues of importance to present and future SNS operation?
This question overlaps with both Charge Questions 2 and 4. The project prioritization and outage planning processes are significant improvements to consolidating activities into a single, coordinated story of what SNS needs to plan to in the coming years. This integrated, documented prioritization and planning process has the potential to improve communications and efficiency.
While the Prioritization Plan does not answer Objective B in its entirety, it is necessary to establish a culture where Objective B can be met, and additionally to understand how to make decisions to meet the objective.
Objective B. Enable success of the Proton Power Upgrade project by providing key technical and management resources as required to meet project objectives.

## Slide 42: Charge Question 6: Is the Beam Test Facility being utilized effectively to address items of importance to present and future SNS operation?
Yes: The Beam Test Facility (BTF) has successfully moved from concept to operation over the last year. The BTF has proven its worth with the qualification testing of the new RFQ.
Emittance, energy and transmission measurements of the new RFQ have been completed reducing the risk associated with the upcoming RFQ swap.
Development of new ion sources, LEBT hardware and operational components have already started. Additional plans are being developed that will extend the use of the BTF proving itself a critical asset for SNS.

## Slide 43: Charge Question 7: Are other test facilities (ISTS, CTF, RFTF, Modulators, etc.) being utilized effectively to address items of importance to present and future SNS operation?
Yes, We saw evidence of this and encourage the on-going use of these important facilities. Test stands maintain operational viability – operational readiness relies upon these facilities and should be treated as a required resource.

## Slide 44: Charge Question 8: Is the SNS response to issues with the existing Inner Reflector Plug (IRP-01) and the IRP under construction (IRP-02) reasonable and adequate? Are there key lessons learned from the IRP-01 and IRP-02 experiences that should be considered in the design and fabrication of the next-generation IRP (IRP-03)?
The SNS response to the issues with the IRP-01 and IRP-02 is quite reasonable and adequate. Thorough investigation of the water leak in IRP-01 enabled development and implementation of a repair plan. The leaking water was rerouted back into the closed loop to avoid accumulation of the liquid waste. This allowed SNS to restart delivery of proton beam with nominal parameters to the target.
A leak has been detected in the IRP-02 at the last stage of fabrication. The root cause of the leak has been identified and reassembly of the IRP-02 is in progress with prudent design modifications.
The SNS target team is designing IRP-03 to incorporate several new features to address lessons learned from operation of IRP-01 and fabrication of IRP-02. They have simplified manufacturing and increased lifetime up to 50 GWh while maintaining the current physics design.

## Slide 45: Charge Question 8: Is the SNS response to issues with the existing Inner Reflector Plug (IRP-01) and the IRP under construction (IRP-02) reasonable and adequate? Are there key lessons learned from the IRP-01 and IRP-02 experiences that should be considered in the design and fabrication of the next-generation IRP (IRP-03)?
Management of the construction of the IRP has been identified as an issue as its construction timeline has stretched to eight years, which is not sustainable in the future. A manufacturing group has been assembled within ISD with the goal of accelerating and improving management of large procurements for technical items such as the IRP as well as targets, beam windows, and other components.
Recommendations (Repeated from target text slides)
Consider PIE of IRP-01 to clarify root cause of the water leak for IRP-03 design.
Work with the vendor to deliver the IRP-02 per current schedule (August 2017) by providing support in engineering, welding, inspection, and leak testing. Actively anticipate any production delays in order to inform scheduling, in case a delay of installation is required.
Consider off-line cryogenic testing of the IRP-02 prior the installation in December 2017.
Consider measures to increase the lifetime of future IRPs.

## Slide 46: Charge Question 9: Is the SNS Target Management Plan a reasonable approach to improving both performance and understanding of SNS mercury targets?
The Target Management Plan the only way to obtain realistic damage information and the greatest promise for future design improvements.
The eventual goals of 1.4 MW, two target changes per year, and no unplanned target changes are appropriate. In the short term, building to 1.4 MW with three target changes per year will be the approach to build confidence. This approach allows implementation of improved target features and collection of PIE data, while supporting a vital user program
However, some uncertainty in the plan’s execution does remain. The mechanism of mitigation by jet flow is not clear. The erosion at corner may not be sufficiently mitigated by only the jet flow. In parallel, the numerical simulations should continue. Margin preserved for irradiation degradation and Liquid Metal Embrittlement (LME). Continue to reconsider the structural design of vessel. PIE is important throughout this process.

## Slide 47: Charge Question 9: Is the SNS Target Management Plan a reasonable approach to improving both performance and understanding of SNS mercury targets?
The plan is a living document, signed-off by division heads. Division heads are aware that additional resources are needed to achieve the plan and have therefore committed to increasing budgets to be consistent with the plan.
Recommendations (Repeated from target text slides)
Management must be vigilant to support the budget needs of the target management plan as it evolves, particularly the support of ancillary activities such as PIE.
Support for PIE has been adequate, and must remain strong. PIE activities should be considered a mandatory part of the target lifecycle, and cannot be avoided or delayed indefinitely.

## Slide 48: Charge Question 10: Is the strategy and schedule for deployment of gas injection in mercury targets reasonable?
Definitely, the He micro-bubble injection has the effect to reduce the cyclic pressure pulse induced by proton beam bombardment. Initial gas injection will be implemented this year with low flow rate, with an upgraded system to come later, perhaps with PPU. Safety assessment is still required for the initial implementation this year with an aggressive schedule. The R&D activities have been extensive, but there is still much work to do even for the initial system. An aggressive approach must be maintained to validate this potentially powerful mitigation.
Recommendation (Repeated from target text slides)
Maintain momentum towards deployment of the gas injection system as an integral part of the Target Management Plan.

## Slide 49: Charge Question 11: Are the SNS responses and ongoing actions to recommendations from the 2016 AAC meeting satisfactory?
The committee saw considerable evidence that the recommendations made in the previous year have been addressed, and followed even with enthusiasm! We are grateful to the SNS staff for responding in this way. Only one remains open.
Some of these recommendations are shown as closed but are acknowledged to be ongoing… this is particularly true in the area of project prioritization. For instance, we encourage more detailed plans involving resource loading and look forward to seeing evidence of this in coming years.